## Design Change Register
Design Change Register - Rockpool Pelican Waters
Address | 90 Spitfire Banks Drive, Pelican Waters Queensland 4551
Project Number | 22066
Date | 16.01.23
Item # | Type of Change | Discipline | Location | Document Reference | Design Change / Departure Details | Reason / Initiator | Contract Drawing Departure | PPR Discrepancy | Variation Required Reference (If Applicable) | Status | Cost Impact | McNab comments | Cost
MILESTONE - DD 75% JULY 2022 | [12 empty] | 85300
1 | Design Change | Architectural | Level 1 | GA | Delete Lift lobby internal door leading into nurses station | Client IFC review | Yes | No | Credit | Documented | 500 | Potential credit to client, however additional framing & sheeting | -500
2 | Design Change | Architectural | Level 1 | GA | Wanderers deck L1 removal of planter. Considered a climbing risk for MSU patients. Was on tender docs. | Client | Yes | No | Credit | Documented | $5-10k | Potential credit to client | -7500
3 | Design Change | Architectural | Ground | GA | Water feature removal (on westside of building) | Client | Yes | No | Credit | Documented | $10k-15k | Potential credit to client | -12500
4 | Design Change | Architectural | Level 1-5 | GA | AWC on each level (in central area) have been amended to now contain either Bath or Quiet room. Odd levels are Quiet room, Even levels are Bath, Level 5 removed entirely. | Client | Yes | No | Credit | Documented | $5k | Potential credit to client | -5000
5 | Design Change | Structural | Level G-Level 2 | STR | Stair and Lift Core walls - Due to the reo requirements of the 290 series Blockwork design being not buildable, the next best option was a 200 thick concrete walls. Our options were building this via insitu, precast, tilts or AFS. Precast lead time was too late, Tilts couldnt get labour from formworker, in-situ would have been 4 cores worth of shutters which the formworker didnt have labour for, or AFS which we could procure in time and install labour was available for our programme. The AFS would only be installed from Ground and Level 1 core walls (to the underside of L2) with the reaminder to be in 290 Block with reduced reo. The hybrid core was not an ideal design and was ultimately the result of the Acor Engineering team NOT initally detailing the reo in full at tender time and also not adopting the suggestions from the ADG Peer review that the 290 series reo could be reduced (and therefore buildable). Acor would not committ to the reduced design and confirmed multiple times they have internally reviewed their modelling and were satisfied it was correct. Cost was around $30-40k with this change Going forward a different Acor engineering team were engaged for Oxley and we are satisfied with the STR design at Oxley. | Design Review | Yes | No | No | Documented | $30-40k | Cost to McNab due to Acor design | 35000
6 | Value Management | Services | All | Services docs | Services risers consolidated / less | Design Review | Yes | No | No | Documented | $5k | Less walls required, less passive fire protection, reduced services path lengths. D&C Services coordination and meetings brought this evolution of the base build design | 5000
7 | Value Management | Structural | Level 5 | STR | Structural columns on Level 5 - removed block shear walls and concrete columns supporting the roof trusses. Changed them to Steell posts (to be fire treated) | McNab DM | Yes | No | No |  |  |  | 0
8 | Value Management | Architectural | All | Frmaing and Wall plans | Wall framing plans - consolidated the wall types to reduce the different sheet types. Reduced it to 4 sheet types (Acoustic, Eco8 Complete, Aquacheck, Standard PB) | McNab DM | Yes | No | No | Documented |  | Cost savings to C&P package | 0
9 | Value Management | Architectural | All | Frmaing and Wall plans | Thermal break tape removed from all external partitions | McNab DM | Yes | No | No | Documented |  | Cost savings to C&P package | 0
10 | Design Development | Architectural | All | Frmaing and Wall plans | Change of flanking detail to ceiling system (same acoustic value RW45 achieved) | Apex | Yes | No | No | Proceeding | Nil | Programme savings | 0
11 | Design Development | Architectural | L5 | RCP | Underslab Insulation now shown on RCPs to ensure Section J details installed | McNab DM | No | No | No | Documented | Nil |  | 0
12 | Design Development | Architectural | All | RCP | Access panels coordinated for services and put on RCPs | McNab DM | No | No | No | Documented | Nil | Reduce risk of AP in wrong position for services | 0
13 | Design Development | Structural | L1-5 | GA | Shear studs added on suspended slabs - this was raised during the peer review and STR drawing reviews by Mcn. The shear studs not being included in the orginal design was an oversight by Acor. | McNab DM | Yes | No | No | Documented | $30K | Acor engineering team changed for Oxley | 30000
14 | Value Management | Electrical | All | Elec | Cable trays removed and use of Catenary support cabling for cables in-ceiling. | Monteur / BSD | Yes | No | No | Documented | Nil | Assists with services spatials. Using catenary cabling is still compliant, however according to STP is not 'best-practice'. Monteur guarantee their work and are liable for it. | 0
15 | Value Management | Mechanical | L1-5 | Mech | Mechanical plant split across Level 1 plant and Roof plant deck - reduced duct, cabling etc for 30% of the mechanical services | Applied Air | Yes | No | No | Documented | Nil | Savings part of the D&C | 0
16 | Value Management | Electrical | Ground | Elec | Electrical main paths to be inground to MSB room, and then inground from MSB to Riser. | Monteur / BSD | Yes | No | No | Documented | Nil | Savings part of the D&C | 0
17 | Value Management | Electrical | All | Elec | Main elec riser moved from Dining room into Comms room. Was sufficient space. | Monteur / BSD | Yes | No | No | Documented | Nil | Savings part of the D&C | 0
18 | Value Management | Architectural | L1-5 | Rooms | Resident room bulkhead above joinery - was originally brought in for enusite exhaust path and created an issue at CARSELDINE by cutting off the pelmet at the window edge. There is sufficnet space to run the exhaust in the ceiling. Therefore we remove the plasterboard bulkhead, replace with a 'bulkhead' in joinery. | McNab DM | Yes | No | No | Documented | TBA | Removal of C&P scope, added in joinery scope. Not sure of the cost savings delta as a result of this. | 0
19 | Design Development | Architectural | Ground | Lift | Lifts BOH Exit - brought about due to lift programming issues at Carseldine not being what RPL Operations want. It is now clear in the OXLEY PPR what they require, however at Carseldine it may not have been clear. Timing wise, this issue has only come up after the Pelican tender and design was completed. The original setup of Pelican was fit for purpose, Rockpool is being quite specific (which we couldnt foresee) on their requirements and therefore adding cost for re-programming. | McNab PM | Yes | No | Yes | Proceeding in principle. Coordination to occur. | $5-10k | Cost / details going through with Kone now. | 7500
20 | Value Management | Architectural | Roof | Roof | Stair and Lift core lids - consolidated what sheeting could be removed and utilise the concrete lid. | McNab DM | Yes | No | No | Documented | TBA | Removal of roof ans teel scope, added in concrete scope. Not sure of the cost savings delta as a result of this. Programme savings as well. | 0
21 | Value Management | Architectural | Roof | Roof | Roof sheeting BMT and type amended to bring into budget (Kliplock where visible, Trimdek on main roof) | McNab DM | Yes | Yes | No | Documented | TBA | Changes accepted to get scope back to budget | 0
22 | Value Management | Architectural | Roof | Roof | Gutter guard removed from main roof as now trees around the building. | McNab DM | Yes | Yes | Credit | Documented | 3000 | Potential credit to client | -3000
23 | Design Development | Architectural | Ground | GA | Exit doors on Ground - Café and Function room - fitout glass had to amend the door hardware and ES added to each. Was documented on Compartmentation drawing, was not let with these as Exit doors. | Architect | No | No | No | Proceeding | $5-7500 | Discovered during door schedule reviews, and BA RFIs. | 6500
24 | Design Change | Architectural | Ground | GA | Ground - outside of laundry and back of maintenance room there was a area of slab on ground removed and additional planting required. Likely cost nuetral | Architect | Yes | No | TBA | Documented | TBA | Likely cost nuetral | 0
25 | Variation | Architectural | Ground | GA | Cafe Terrace Entry - Major changes after the client IFC review. Want this to be the centre piece of street frontage and link the café to the foothpath. | Client | Yes | No | TBA | Documented | TBA | Pricing up as of 20.1.23 | 0
26 | Variation | Kitchen/Laundry/Waste | Ground | GA | Group Schedule changes - due to UFD not updating the group schedule during the Carseldine build phase, changes that were made there did not get brought over to PW group schedule. This was discovered during a schedule review with the client. | McNab DM | Yes | No | TBA | Documented | TBA | There were debits/credits throughout and the big ticket item is the Ewater. See below | 0
27 | Design Development | Architectural | Ground | GA | Falls added to open Fire stairs to send water out from landings. Add in drainage at base of stair well. | McNab DM | Yes | No | No | Documented | Nil |  | 0
28 | Design Development | Architectural | Roof | GA | Roof plant deck raised 150mm in order to allow for mechanical services paths on the underside of plant slab. Arch didn’t allow for insulation and ceiling framing (150mm total) in this zone. | McNab DM | Yes | No | No | Documented | TBA | Internal risk | 0
29 | Variation | Architectural | Ground | GA | Flagpoles added at ground level front of site after contract sum submission. | Client | Yes | Yes | Yes | Documented | 6000 |  | 0
30 | Variation | Architectural | L1-5 | GA | Interconnecting SOU doors added after tender. Client argues they were installed at CARSELDINE, but Architect did not document for PW. PPR does not mention a requirement for interconnecting doors. McNab is not privy to client and architect decisions on room types quantities. | Client | Yes | Yes | Yes | Documented | 17000 |  | 17000
31 | Variation | Architectural | Ground | GA | Ewater changed to a McNab supply item in Group schedule AFTER tender submission for PW. At Carseldine it was advised the clients supplier advised he couldn’t get it. McNab then agreed to supply it (at our cost of $10k) despite the supply clearly not being on us. Due to this happening at CARSELDINE, client is maintaing we should have allowed for it at PW (Group schedule was a 2 item in our tender submission). | Client | Yes | Yes | Yes | Documented | 10000 |  | 10000
32 | Variation | Architectural | Ground | GA | Wall vinyl to laundry chute room - At the time of tender McNab confirmed in a tender clarification that “Due to discrepancy between the PPR and the Interior Finishes Design, McNab confirms this tender includes wall vinyl as per the PPR”. McNab has been advised that wall vinyl be allowed for in the Chute room, in addition to areas listed in the PPR. | Client | Yes | Yes | V08 | Documented | 2800 |  | 2800
33 | Variation | Architectural | L1 | GA | Crimsafe screens added to wanderers deck | Client | Yes | No | V17 | Documented | 3861 |  | 0
34 | Variation | Architectural | L1-5 | GA | Handwashing joinery in corridors - addition after | Client | Yes | No | V14 | Documented | 13750 |  | 0
35 | Variation | Architectural | L1-5 | GA | Soft close hinges - added | Client | Yes | Yes | Yes | Documented | TBA |  | 0
36 | Variation | Electrical | Ground | Elec | Switchboard upgrade upgrade due to energex requirements | McNab | Yes | No | V13 | Documented | 8079 |  | 0
37 | Variation | Architectural | L1-5 | GA | Western façade windows added after tender | Client | Yes | No | V12 | Documented | 48950 |  | 0
38 | Variation | Landscape | Ground | GA | OPW - Landscape added due to Council changes | Client | Yes | No | V08 | Documented | 1102 |  | 0
39 | Variation | Architectural | Ground | GA | Laundry heat pump changed from electric dryers - change to hydraulics | Client | Yes | Yes | V07 | Documented | 6178 | MCN value managed the hydraulic to remove the UFD specified drain | 0
40 | Design Change | Architectural | Ground | GA | Kitchen and Laundry flooring type changed from vinyl to epxoy. Enables a change in the drain types to be a flip lid, not a screw lid which needs to clamp onto the vinyl. | Client | Yes | Yes | Yes | Rockpool to confirm if proceeding |  | Cost neutral | 0
41 | Variation | Architectural | All | GA | Interiors schedule updated after tedner submission - various changes | Client | Yes | Yes | Yes | Proceeding | TBA |  | 0
42 | Variation | Architectural | S2 | L1-5 | S2 rooms - added vinyl strip to tea making facility in room. 5 rooms in total | Client | Yes | No | Yes | Proceeding | TBA | Added in December after vinyl package was let. | 0
43 | TBC | Electrical | Roof | Roof | Solar panels not connected to the grid (energex cancelled application). Therefore RPL operated without solar for 6 months plus. | TBA | No | No | No | Proceeding | TBA | Potential counted claim from RPL | 0
44 | TBC | Electrical | Hobby Shed | Architectural | Reduce Motorised Roller doors from 2 to 1. Only Hobby Shed required to be Motorised now, Bin and Maintenance Shed to be manual. | Client | No | Yes | No | Proceeding | 466 | Potential credit to client

## Data
Type of Change | Discipline | Contract Drawing Departure | PPR Discrepancy | Status | Cost Impact
Design Change | Architectural | Yes | Yes | Being documented | Nil
Variation | Civil | No | No | Rockpool to confirm if proceeding | NA
Design Development | Hydraulic | NA | NA | Not Proceeding | TBA
TBC | Structural |  |  | Proceeding | Minor cost
Value Management | Mechanical |  |  | Proceeding in principle. Coordination to occur. | Major cost above 10k
| Fire |  |  | Documented
Acoustic
Sustainability
VT
Landscape
Survey
Traffic
Interior
Kitchen/Laundry/Waste
Electrical
NCC Section J
Nurse Call
Services