Inspection Template: ITP: Passive Fire 03.36

Fire Doors / Frames / Hardware

Confirm manufactures door set is compliant with tested wall system: Upload Manufacturer’s specification and test results

Fire rating / filling requirement of frame: Manufacturer's specification / AS 1905.1

Correct fire rated frame installed plumb and level: Check frame filled and 25mm stop on frame

Frame sealed to floor substrate: Upload photos

Fixings installed as per Manufacturer's recommendations including size / gauge and distances: Upload photos

Doors only measured after floor finish installed or written agreed heights with floor and door subcontractors: Upload written agreement                                                correspondence to subcontractors here

Door and hardware only installed by licensed carpenter as per BCA: Upload license here

Caps to door / frame/ floor checked and compliant with Manufacturer's tested system: Specify gaps here as per AS1905.1 or         manufactures test requirement

Doors and frames inspected and tagged: Upload all applicable documents here

Walls & Ceilings

Framing installed with Noggins and corner angles: Upload details and photos, No timber allowed in fire walls

Seismic fixings installed: As per AS 1170.4: Upload photos

Wall junctions as per Manufacturer's detail: Upload photos

Sarking installed has Flammable index and identification facing inwards AS1530.2: Upload photos

Fire boxes installed in walls: Upload photos, upload Manufacturer's data

Ceiling framing as per Manufacturer's system for fixings: Upload photos

Base Metal Thickness (BMT) of framing as per tested system: Check against tested system requirement

Sheet joints staggered: Upload photos showing distances

Vertical and horizontal fire separation as per NCC-2.6: Upload photos

Rockwool installed to U/S roof sheeting and/or cavities: Upload photos

Fire walls complete and ready for McNab inspection before sheeting

All fixings and joints are set: Upload photos

All sheeting abutting other surfaces is fire rated/ sealed: Upload photos

Services Penetrations

Sample board set up and approved for all fire rating requirements: Arrange 3rd party inspection with Quality

Fire collars and wraps have a current test certificate: Upload current test certificates

Fire mastics have current test data and are compliant with test: Upload current test certificates

Services are minimal 100mm from combustible surface: Upload photos

Fire penetrations inspected and sticker attached: Upload photos and register

Setting sub-contractor

Joints taped, base coat, top coat complete (Photos attached).

Walls and ceilings sanded, free of blemishes ready for sealer coat.

Floors Scraped units cleaned (photos required).

(HOLD POINT) Inspection with McNab ahead of the painter.