## Matrix
BA for Rockpool Pelican Waters - B220407-2
Project Number |  | 22066
Project Name |  | Rockpool Pelican Waters
Date |  | 17.01.2023
COND | DESCRIPTION |  | TIMING | STATUS | RESPONSIBLE | Comments
Part C - Approval Conditions and Notes
Section B - Structure
B1 | All structural work is to be completed in accordance with the approved plans and/or site instructions issued by the Structural Engineer during inspections of the various components. |  | During Construction |  | McNab
B2 | Timber engineering certification for prefabricated timber elements (IE. Roof trusses, frames, lintels, etc) as applicable, shall be provided to the Building Certifier prior to frame inspection for assessment. |  | During Construction |  | McNab
B3 | Non-structural parts and components and their fastenings shall be designed for horizontal and vertical earthquake forces in accordance with section 8 of AS1170.4. |  | During Design |  | ACOR Consultants
Section C - Fire Resistance
C1 | This building approval has been the subject of a performance solution as outlined by the Fire Engineer for the following items:-
BCA Clause C2.5 - Ground floor smoke compartment exceeding 500sqm
BCA Spec C3.4 - single directional smoke doors
BCA Clause D1.8 - Closure of lowest level of Open stairs for security
BCA E1.5 - Removal of sprinkler from lot of lift shaft as noted in AS2118.1
C 2 | The Steel columns and wall beams in the external walls must obtain a minimum FRL of 120/120/120 by a system tested and installed in accordance with AS1530.4. |  |  |  | McNab
C 3 | The Chutes have been constructed as an extenion of the Grd Floor thus requiring the bounding walls to be be 120/120/120FRL in both directions in accordance with BCA Clause C2.7. The top of these chutes must be capped or constructed to comply with BCA Clause D2.7 |  |  |  | McNab
C 4 | All lightweight construction used for fire rated walls must comply with BCA Clause C1.8 & BCA Spec C1.1. Details and specifications of the products demonstrating compliant tested systems must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  |  |  | McNab
C 5 | All materials and assemblies shall comply with the Fire Hazard Properties as outlined in BCA Clause C1.10 and Specification C1.10 & C1.10a. Details and specifications of the products showing compliance with the required Properties must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  |  |  | McNab
C 6 | All Ancillary Elements must comply with C1.14. Sunshades, screens and gate shall be non-combustible construction.
C 7 | Installation certification for any passive fire rated system must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | McNab
C 8 | The building must be divided into compartmentation complying with BCA Clause C2.5 and the FER Performance Solution (as applicable) for both fire and smoke separation. |  |  |  | GJG Architects
C 9 | The smoke walls in this building must have non-combustible wall linings. The wall linings must not be penetrated by any combustible material (ie. Timber) and any penetration must be sealed with an appropriately rated material. Installation of the passive smoke protection must be certified prior to the Certificate of Occupancy being issued. |  |  |  | McNab
C 10 | Vertical separation of any external wall cavity must be sealed at the line of the FRL horizontal barrier by a FRL tested or non-combustible material in accordance with BCA Clause C2.6. The installation certificate of a Passive Fire Rated System must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | McNab
C 11 | Lift shaft construction to maintain an FRL of not less than 120/120/120 with openings suitably protected. Lift doors to be a minimum of -/60/-. |  |  |  | McNab
C 12 | Openings in the external walls between compartments must be protected by a method nominated with BCA Clause C3.4. A Passive Fire Rated System must have an installation certificate supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | McNab
C 13 | A fire rated door must be installed in accordance with BCA Specification C3.4 and the manufacturers tested prototype. Installation certification stating that the installed door is in accordance with the manufacturer’s specification must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. The fire door and frame must also be tagged to demonstrate Australian Standard compliance. |  | Before COC |  | McNab
C 14 | A fire rated door required by BCA Clause C2.5 must be provided with a 400mm smoke reservoir directly above the doorway. |  |  |  | McNab
C 15 | A smoke door must be installed in accordance with BCA Specification C3.4 including being a solid core door with a minimum door thickness of 35mm. The door must be fitted with a smoke detector within 1.5m of each side of the doorway and be provided with a minimum 400mm smoke reservoir on each side. |  |  |  | McNab
C 16 | Smoke doors must be installed as per the FER for directional swing requirements and appropriate door hardware. |  |  |  | McNab
C 17 | Services other than those listed in C3.9 are not permitted to penetrate the fire isolated stairs. |  |  |  | McNab
C 18 | Doorways in lift shafts must be protected by --/60/-- fire doors set to remain closed except when discharging or receiving passengers, goods or vehicles in accordance with AS1735.11. |  |  |  | McNab
C 19 | Penetrations for service installations shall be in accordance with BCA Clause C3.15 & Specification C3.15. Installation certification for the various system must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | McNab
C 20 | Where a duct passes through an element used for both smoke and fire separation (eg. floors), the duct must be fitted with a combination damper to restrict the spread of smoke and fire through the duct. |  |  |  | McNab
C 21 | Any existing fire rated walls must not be compromised. Any penetrations or openings for services in the existing fire rated walls shall be sealed in accordance with BCA Clause C3.15 & Specification C3.15. Installation certification for the various system must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | McNab
C 22 | Construction joints, spaces and the like in and between building elements required to be fire rated (eg. external cladding cavities between walls & floors) must be protected with a suitable tested system to achieve the required FRL. |  |  |  | McNab
C 23 | External walls (all elements) must be constructed with non-combustible material as determined by AS1530.1 and includes the following elements; framing, insulation, linings, external cladding etc. Similarly, awnings, screens and similar attachments must be non-combustible or comply with the requirements in BCA C1.14. Product test certificates and specifications must be provided to the Building Certifier for approval prior to installation. |  |  |  | McNab
Section D - Access and Egress
D1 | The Level 1 Hydraulic Plant room must have the door relocated to reduce the maximum travel to a point of choice to a maximum 20m. |  | During Design |  | GJG Architects
D2 | Doorways must provide an unobstructed width of not less than 1070mm into sole-occupancy units, 870mm in other resident use areas and 800mm in non-resident use areas. All other provisions of BCA Clause D1.6 must be adhered to. |  | During Design |  | GJG Architects
D3 | The building is to be provided with minimum public corridor widths of 1.5m clear between obstructions. And increased to 1.8m clear for the full width of the doorway leading into sole-occupancy units or communal bathrooms. |  | During Design |  | GJG Architects
D4 | A minimum of 1 side of the external stairs (in-lieu of fire-isolated stairs) must remain open at all times for ventilation to the outside air. This requires the unobstructed opening to to be no less than the sqm of the access doorway landing. The open area can be calculated from 1m above the landing to allow for solid balustrading. It must not be enclosed with weather protection screens, or similar, that restrict the free air movement by greater than 25%. The upper ceiling level of the external stairway must be constructed to allow smoke to vent externally and not be trapped within the stairway (No down turn on the outer edge that traps smoke to a depth that it can re-enter the building). |  | During Design |  | GJG Architects
D5 | The ground floor level of the external stair has been the subject of a Fire Engineered Performance Solution to allow it to be enclosed on the external face for security. |  | During Design | N/A
D6 | Access to the lift pits must be through the lowest landing doors in accordance with BCA Clause D1.17. |  | During Design |  | GJG Architects
D7 | All electrical distribution boards and telecommunications boards must be enclosed within non-combustible construction and have any openings or accesses sealed to prevent the free passage of smoke. Alternatively the boards can be contained within cupboards that are lined with a fire protective covering and have all doorways and openings sealed against smoke spreading from the enclosure. Compliance with BCA Clause D2.7 for all installations in paths of travel must be obtained. |  | During Design |  | GJG Architects
D8 | Stair geometry shall be in accordance with BCA Clause D2.13 including maximum and minimum tread width and riser height, and number of risers within a flight. Also the risers must not allow a 125mm-diameter sphere to pass through. |  | During Design |  | GJG Architects
D9 | Stair nosings must comply with AS1428.2009 Clause 11. At the nosing each tread shall have a strip not less than 50mm and not more than 75mm deep across the full width of the path of travel. The strip may be setback a maximum of 15mm from the front of the nosing. The strip shall have a minimum luminance contrast of 30% to the background. Where the luminance contrasting strip is not set back from the front of the nosing then any area of luminance contrast shall not extend down the riser more than 10mm. |  | During Design |  | GJG Architects
D10 | Treads and nosings are to be slip-resistant in accordance to Table D2.14 when tested in accordance with AS4586. |  | During Design |  | GJG Architects
D11 | Door thresholds shall be in accordance with BCA Clause D2.15 to not incorporate a step within a radial distance of the door leaf. If a rise or fall is unavoidable within the threshold, a ramp can be provided but must not exceed a maximum gradient of 1:8 for a maximum height of 25mm. |  | During Design |  | GJG Architects
D12 | Where there is a fall of 1m or more to the surface beneath, balustrades shall be provided at a minimum of 1m in height and have no openings that will allow the passage of 125mm-diameter sphere to penetrate in accordance with BCA Clause D2.16. |  | During Design |  | GJG Architects
D13 | Balustrades shall not incorporate climbable elements between the heights of 150mm and 760mm on a barrier to a floor more than 4m above the surface beneath. |  | During Design |  | GJG Architects
D14 | Handrails to the stairs shall be installed in accordance with BCA Clause D2.17 including mounting height and clearance from walls. A handrail must also be provided along one side of a ramp or flight of stairs. |  | During Design |  | GJG Architects
D15 | Ladder access to roof plant shall be constructed in accordance with AS1657-2013. |  | During Design |  | GJG Architects
D16 | The sliding exit doors must be able to be opened manually under a force not exceeding 110N and if power operated must fail open in the event of a power failure to the door or activiation of alarms in that compartment, in accordance with BCA Clause D2.19. |  | During Design |  | GJG Architects
D17 | All doors required to achieve an FRL have been assessed as part of a Fire Engineered Alternative Building Solution to swing against the direction of egress. As a requirement of the Fire Engineer Report these doors shall be fitted with signage to the non-compliant side stating "FIRE SAFETY DOOR - PULL TO EXIT". |  | During Design |  | GJG Architects
D18 | All exit doors and doors in paths of travel to an exit must be openable by using a single pushing or downward hand action in accordance with BCA Clause D2.21. Alternatively the door can be connected to the FDCIE for automatic release of latches upon activation of the FDCIE. NOTE: In this regard a door may be fitted with an automatic fail-safe device which unlocks the door on activation of any sprinkler or smoke detection system in the building. |  | During Design |  | GJG Architects
D19 | The doors to the external stair are not to be locked from the stair side or shall have automatically unlocking devices connected to the fire detection and suppression systems. |  | During Design |  | GJG Architects
D20 | All exits into fire-separated stairways, fire and smoke doors shall be provided with door signage in accordance with BCA Clause D2.23. The door signs must be door type specific. ie. For automatic doors with hold open devices (“FIRE SAFETY DOOR - DO NOT OBSTRUCT”). For self-closing doors (“FIRE SAFETY DOOR - DO NOT OBSTRUCT - DO NOT KEEP OPEN”). For a door discharging from a fire-isolated exit ("FIRE SAFETY DOOR - DO NOT OBSTRUCT") |  | During Design |  | GJG Architects
D21 | All windows with openable components below 865mm from the floor, with a falling distance of 4m to the external surface beneath, must be fitted with a restricting device to ensure the openable portion of the windows does not exceed 125mm. Alternatively the window can be fitted with a protection that does not have any openings exceeding 125mm resisting 250N of force and certificates provided upon completion. |  | During Design |  | GJG Architects
D22 | The building has been the subject of a Performance Solution to allow a variation from the BCA DtS Provisions for the requirement of compliance with AS1428.1 for: a) Allowing resident rooms and ensuites to have minor variations to AS1428.1-2009 for fixtures and fittings and no specific bedroom designed to AS1428.1. b) Allowing the use of an Alternative Pan for compliance with AS1428.1 toilets that do not have a backrest |  | During Design |  | GJG Architects
D23 | Access to and within the building for people with disabilities shall be provided in accordance with BCA Clause D3.2 and AS1428.1-2009. This building is required to have accessible doors include a contrasting leaf, architrave or wall in accordance with AS 1428.1. |  | During Design |  | GJG Architects
D24 | Car parking for people with disabilities shall be provided in accordance with BCA Clause D3.5 and AS2890 including lines at top and bottom. |  | During Design |  | GJG Architects
D25 | Identification of access for persons with disabilities to concealed front entries and internal public facilities shall be in accordance with BCA Clause D3.6 & Specification D3.6. AS1428.1 signage for PWD fixtures will only be accepted on fully compliant fixtures. All other facilitties will need standard toilet fixture signage |  | During Design |  | GJG Architects
D26 | Identification of the exits shall be in accordance with BCA Clause D3.6 and Specification D3.6, requiring a braille and tactile sign to state EXIT and be located as indicated in BCA Specification D3.6. |  | During Design |  | GJG Architects
D27 | Tactile indicators are required to warn vision impaired people that they are approaching areas stated under BCA Clause D3.8. Indicators will need to comply with AS1428.1 or AS1428.4 depending on the Australian Standard outlined in BCA Clause D3.8. This specifically relates to the main entry junction with the vehicular drop-off area. |  | During Design |  | GJG Architects
D28 | All new glazing on an accessway, capable of being mistaken for a doorway or opening, must be clearly marked in accordance with AS1428.1-2009. |  | During Design |  | GJG Architects
Section E - Services and Equipment
E1 | The fire hydrants must be installed to comply with BCA Clause E1.3 and AS2419.1 including water flow and pressure requirements. Installation and commissioning certification must be submitted to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | STP Consultants
E2 | The fire sprinkler system must be installed in accordance with BCA E1.5 and AS2118.1. The main valve assembly must be provided with a local alarm and connected to the FDCIE via a second input to the ASE installed. A block plan must be provided to illustrate the system. Installation and commissioning certification must be submitted to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | STP Consultants
E3 | The fire sprinkler system must activate the building occupant warning system. The main stop valve must be monitored by the Fire Service. A Main Stop Valve is the stop valve located in the Sprinkler Valve Assembly and not any other valves upstream of that location. |  | Before COC |  | STP Consultants
E4 | The fire sprinkler system has been the subject of a performance solution allowing the removal of the sprinkler head from the top of the lift shaft |  | Before COC |  | STP Consultants
E5 | Portable fire extinguishers shall be provided and installed in accordance with BCA Clause E1.6 and AS2444. |  | Before COC |  | McNab
E6 | Provide suitable fire fighting equipment on site during construction as per BCA Clause E1.9. This includes Fire Extinguishers on each storey, and operational Fire Hydrants and FHR's (where required) once the building reaches an effective height of 12m. |  | During Construction |  | McNab
E7 | Smoke detection must be provided throughout the building in accordance with BCA Clause E2.2 and AS1670.1. Installation and commissioning certification must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | STP Consultants
E8 | The detection system must activate an occupant warning system complying with Clause 3.22 of AS1670.1 throughout all areas of the occupied building. A minimum sound pressure level of 75dB(A) must be obtained at each bed head in accordance with AS1670.1. The system has been established to allow cascading in accordance with AS1670.3 however the cascading must be set at a maximum Alert time of 3mins before moving to Evacuation. |  | Before COC |  | STP Consultants
E9 | The smoke detection system must be provided with mimic panels or annunciator panels with alpha numeric displays in each smoke compartment to provide automatic indication of each zone or display setting of the FDCIE as required by BCA Specification E2.2a. |  | Before COC |  | STP Consultants
E10 | Manual call points must be provided throughout the facility in locations ensuring that no point of the floor is more than 30m from a call point. |  | Before COC |  | STP Consultants
E11 | The lifts must be installed to comply with AS1735 and Part E3 of the BCA. They must be provided with a warning sign against the use of the lift in a fire on all lifts except those only used for the transportation of goods. A passenger lift must have compliance with AS1735.12 for items nominated in Clause E3.6 of the BCA. |  | Before COC |  | STP Consultants
E12 | The lift must be provided with a stretcher facility that has dimensions compatible with BCA Clause E3.2. |  | Before COC |  | STP Consultants
E13 | Passenger lifts must have warning signs installed reading "Do not use lifts if there is a fire" and be installed in accordance with BCA Clause E3.3. |  | Before COC |  | STP Consultants
E14 | The lifts must be provided with fire service controls in accordance with AS1735 Parts 1 & 2 and BCA Clause E3.7. |  | Before COC |  | STP Consultants
E15 | Emergency Lighting and Illuminated Exit Signs shall be installed in accordance with BCA Part E4 and AS2293.1. Installation and testing certification must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | STP Consultants
Section F - Health and Amenity
F1 | The building has been the subject of an Alternative Solution to allow a variation from the BCA DTS Provisions for: a) External wall construction and weatherproofing. |  |  | N/A
F2 | Stormwater drainage must comply with AS3500.3. |  |  |  | ACOR Consultants
F3 | Waterproofing membranes for external above ground use must comply with AS4654 Parts 1 & 2. |  |  |  | McNab & GJG Architects
F4 | Prevention of the penetration of water through external walls has been reviewed against FP1.4 and deemed satisfactory for their intended use. |  |  | N/A
F5 | Sarking-type materials used for weatherproofing of roofs and walls must comply with AS4200 Parts 1 & 2. |  |  |  | McNab & GJG Architects
F6 | Waterproofing to wet areas shall be provided in accordance with BCA Clause F1.7 and AS3740. |  |  |  | McNab & GJG Architects
F7 | All glazing assemblies in external walls shall comply with AS2047 and are limited to those specific assemblies noted in BCA Clause F1.13. |  |  |  | McNab & GJG Architects
F8 | The building shall be provided with a fixed or mobile bath to service the residents of the building. |  |  |  | GJG Architects
F9 | A Performance Solution has been accepted for the provision a disinfaction assembly in lieu of a slop hopper. |  |  | N/A
F10 | Clinical hand wash basins must be provided for the building at a minimum rate of 1 per 16 residents. |  |  |  | GJG Architects
F11 | Construction of the Required disabled person’s sanitary compartment shall be in accordance with AS 1428.1 (Except for the toilet pan variation) and BCA F2.4 including circulation requirements, fixtures, fittings and the installation of a shelf. Also adequate facility for disposal of sanitary towels must be provided. |  |  |  | GJG Architects
F12 | Construction of sanitary compartments shall be in accordance BCA Clause F2.5 including door swing direction or lift-off hinges. |  |  |  | McNab & GJG Architects
F13 | This building has been the subject of a Performance Solution allowing the use of a care specific toilet arrangement instead of a compliant AS1428.1 toilet. |  |  | N/A
F14 | Natural ventilation is required for the resident bedrooms and shall be maintained. Openable windows will need to maintain compatability with acoustic performance in the acoustic report referenced in the MCU. |  |  |  | McNab
F15 | Artificial lighting shall comply with BCA Clause F4.4 and AS/NZS1680.0. |  |  |  | STP Consultants
F16 | Mechanical ventilation shall be installed in accordance with BCA Clause F4.5 and AS1668.2 or AS/NZS3666.1. Installation and testing certification must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | McNab
F17 | All required natural ventilation to bedrooms must be provided by doors and windows that comply with the DA Acoustic Report ensuring the building has the same outcomes as the DA requirements. |  |  |  | McNab & GJG Architects
F18 | Mechanical ventilation installed in the commercial kitchen exhaust hood shall comply with AS/NZS1668.1 and BCA Clause F4.12. |  |  |  | McNab & STP
F19 | Sound transmission for the building between units shall be in accordance with BCA Clause F5.3, F5.4, F5.5 and F5.6. Acoustic walls are to be continuous for all elements (frame, insluation and linings) for floor to the underside of the floor above or the underside of the roof sheet. |  |  |  | McNab & GJG Architects
F20 | Internal services require acoustic separation in accordance with BCA F5.6 including at least Rw 40 in habitable rooms (SOU's) and RW 25 for non-habitable rooms such as ensuites. |  | Before COC |  | McNab & GJG Architects
F21 | The door between the SOU bedrooms has been the subject of a Performance Solution allowing a non-sound tested 35mm min thick solid core door with acoutsic seals to be used in luie of a tested system. |  |  | N/A
F22 | All mechanical design systems and elements must comply with the Acoustic Report completed with the DA. The Installation Contractors must confirm compliance with the Design Report Outcomes when providing an Installation Certification for their various elements |  |  |  | McNab
Section G - Ancillary Provisions
G1 | The cold rooms and freezers shall be provided with life safety features as outlined in BCA Clause G1.2. These include a door capable of being opened from the inside without a key, and internal light activated by a light switch located internal adjacent to the door and an external indicator lamp that illuminates when the internal light is on, and an alarm located external of the room but activated from inside the room that achieves the necessary dBa minimum requirement. |  | Before COC |  | McNab
Section J - Energey Efficiency
J1 | Compliance with BCA Section J has been established using the BCA Verification Method JV3 demonstrating acceptable outcomes. All items of the report requirements must be implemented and installation certificates for each aspect must be provided to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | McNab
J2 | Energy efficiency elements to be installed in accordance with J1 including tight fit, continuous with taping and/or lapping where reqiured. |  |  |  | McNab
J3 | Construction of energy efficiency wall materials to be continuous from slab to slab including insulation and plasterboard in the concealed spaces. |  |  |  | GJG Architects
J4 | The external glazing must be supplied and installed to obtain the minimum thermal requirements as outlined in JV3 Report and installed in accordance with the BCA. Supplier’s certification for the glazing elements nominating the Solar Heat Gain Coefficient for the elements supplied. |  |  |  | Cundall
J5 | The envelope/s of the building must be sealed in accordance with the provisions of Part J3 of the BCA. Details of the installations must be supplied to the Building Certifier prior to the Certificate of Occupancy being issued. |  | Before COC |  | McNab
J6 | All hot water systems must be installed in accordance with Section 8 of AS/NZS3500.4 and Clause J7.2 of the BCA. |  |  |  | McNab
J7 | The building must be provided with the facility to record individually the energy consumption of various components in accordance with BCA Clause F8.3. |  |  |  | STP Consultants
General Conditions
1 | In accordance with the Building Act 1975 Clause 114(2) occupation of this building is not permitted, until a Certificate of Occupancy has been issued. This certificate is issued when the works have reached the stage of substantially completed and is dependent upon certificates supplied to the Building Certifier as noted in Part D of this Notice. |  |  |  | McNab
2 | The approval for this development permit for building work shall lapse if the building work is not commenced within 2 years after the date of this approval; and completed within 3 years after the date of this approval. |  |  | N/A | McNab
3 | The applicant for this development must ensure that 1 legible set of current drawings for the development is available for inspection on the building site while the building work is in progress. |  | During Construction |  | McNab
4 | Provide one set of “as constructed” plans prior to or at final inspection, including a list of Fire Safety Installations in accordance with Section 102 of the Building Act for forwarding to the Queensland Fire & Emergency Service. |  | During Construction |  | McNab
5 | It is acknowledged that alteration and amendments may occur during construction. Applicable revised drawings and certificates shall be provided for assessment and approval. The issuing of a Certificate of Occupancy will not be considered until documents reflecting these changes have been provided. |  | During Construction |  | McNab
6 | This building must comply with the requirements of Evacuation Support as outlined within QDC MP2.2. A detailed Emeregncy Plan and assocatied parts must be implemented at time of the Final Insepction demosntrating the ability for compliance to be maintained. |  | During Construction |  | McNab
7 | Compliance with any endorsements on the approved documentation shown in RED. |  |  | N/A | McNab
8 | This approval is to be read in conjunction with the previous Staged Approval B220407-1 issued by Formiga1. |  |  | N/A
Inspections
9 | This practice has accepted that an appropriately registered professional engineer will be undertaking Footing, Slab and Framing inspections. Certificates of inspections shall be forwarded to this practice within 3 working days of inspections being carried out. Certificates shall state that the inspected works are in accordance with approved documents. |  | During Construction |  | McNab & STP
10 | Specific inspections regarding fire/smoke rated elements, sound rated elements, preliminary final and final inspection shall be carried out by this practice. A minimum of 5 days’ notice shall be observed. |  | Before COC |  | McNab
11 | A final inspection shall be carried out by this practice in conjunction with QFES. This inspection will be arranged directly with QFES by this practice. A minimum of 20 business days notice shall be observed. |  | Before COC |  | McNab
Advisory Notes (These are not conditions of approval)
a | QBCC Subsidence Policy: The building work approved under this Development Permit has not been assessed against the Queensland Building and Construction Commission policy relating to subsidence. |  | N/A
b | This approval does not include plumbing and drainage work. Vehicular access, builders sanitary, and other statutory fees required by local authorities have not been included in the fee proposal and may be invoiced directly from the local government to owner. |  | N/A
c | Operational Work: This approval does not include approval of any earthworks (cut or fill) not associated with, or incidental to, the proposed building work. Such work, if proposed by the applicant, may require additional approval from the local authority. |  | N/A
d | Fire Ants: The building certifier recommends that you check with the Department of Primary Industries (www.dpi.qld.gov.au or phone 13 25 23) to ascertain whether the property is located within a Fire Ant Restricted Area, prior to carrying out any work on site. |  | N/A
e | Retaining Walls and Fences: This building development approval does not include the approval of ASSESSABLE retaining walls and/or fences unless specifically described on the Decision Notice and the associated approval documentation. |  | N/A
Part D - Certificate of Classification
| The following certificates must be provided to the Building Certifier in a single submission with all forms completed in accordance with Clause 48 of the Building Regulation 2006. QBCC Licences shall also be provided for all contractors for competency in that class of work. Incorrect forms will be returned for re-submission. |  |  |  | McNab
| In accordance with the Building Act 1975 Clause 114(2) occupation of this building is not permitted, until a Certificate of Occupancy has been issued. This certificate is issued when the works have reached the stage of substantially completed and is dependent upon: |  |  |  | McNab
a | Satisfaction of all conditions nominated in association with the review of this application; |  |  |  | McNab
b | Satisfaction of the requirements in regard to inspections; |  |  |  | McNab
c | Submission of a copy of the Drainage Clearance Certificate as issued by the relevant local Government; |  |  |  | McNab
d | Certificates generally to be provided: |  |  |  | McNab
1 | Evidence that the Commissioner of the Queensland Fire and Emergency Services is satisfied with the provision, installation and operation of the Special Fire Services; |  | Before COC |  | McNab
2 | Provide "As Constructed" plans showing the locations of the all special fire services in the building(s) (Items that are Subject to Referral Advice to the QFES); |  | Before COC |  | McNab
3 | Provide a list for the Fire Safety installations in the building and plans showing their locations (Refer Building Act 1975 Definition for Fire Safety Installations); |  | Before COC |  | McNab
4 | Structural engineers design and inspection certification for all Design & Construct aspects; |  | Before COC |  | McNab
5 | Structural engineers inspection certification for all structural elements; |  | Before COC |  | McNab
6 | Surveyors set out certificate stating set out is in accordance with the approved plans and the Development Approval; |  | Before COC |  | McNab
7 | Details and Specification for assemblies and floor coverings showing Fire Hazard Properties compliance with BCA Specification C1.10; |  | Before COC |  | McNab
8 | Test certificates and specifications for the non-combustible building elements in accordance with AS1530.1. |  | Before COC |  | McNab
9 | Passive fire system installation certification for the walls nominating the products used, the FRL obtained, and installation compliance with the manufacturers specification; |  | Before COC |  | McNab
10 | Fire door installation certification nominating the products used, the FRL obtained and installation compliance with the manufacturer's specification; |  | Before COC |  | McNab
11 | Installation certification for the passive fire penetrations through fire rated elements and compliance with the manufacturer's specification; |  | Before COC |  | McNab
12 | Installation certification for the mechanical penetrations through fire rated elements and compliance with the manufacturer's specification; |  | Before COC |  | McNab
13 | Installation certification for the passive smoke wall construction and compliance with the manufacturer's specification; |  | Before COC |  | McNab
14 | Installation certification for the smoke doors nominating the products used and installation compliance in accordance with manufacturer's specifications; |  | Before COC |  | McNab
15 | Installation certification for the penetrations through smoke walls, nominating the products used and compliance with the manufacturer's specification; |  | Before COC |  | McNab
16 | Installation certification for the mechanical penetrations through smoke walls and compliance with the manufacturer's specification; |  | Before COC |  | McNab
17 | Installation and commissioning certificates for the fire hydrants stating compliance with AS2419.1 and nominating the achieved water flow and pressure; |  | Before COC |  | McNab
18 | Installation certificate for the fire extinguishers stating compliance with AS2444. |  | Before COC |  | McNab
19 | Installation and commissioning certificates for the fire sprinkler system stating compliance with AS2118.1 and nominating the achieved design flow rates; |  | Before COC |  | McNab
20 | Installation and commissioning certificates for the smoke detection system stating compliance with AS1670.1; |  | Before COC |  | McNab
21 | Installation and testing certificate for the emergency lighting and exit signage stating compliance with AS2293.1; |  | Before COC |  | McNab
22 | Installation and commissioning certificate for the lift installation stating compliance with the relevant sections of AS1735; |  | Before COC |  | McNab
23 | Installation and testing certification for the mechanical ventilation systems stating compliance with AS1668 Parts 1 & 2; |  | Before COC |  | McNab
24 | Installation certification for the waterproofing of wet areas stating compliance with AS3740; |  | Before COC |  | McNab
25 | Suppliers certification for the glazing assemblies stating compliance with AS2047; |  | Before COC |  | McNab
26 | Installation certification for the sound rating nominating the products used, the Rw obtained and installation in accordance with the manufacturer's specification; |  | Before COC |  | McNab
27 | Installation certification for the various components of the Energy Efficiency systems/products used, stating installation compliance with the manufacturer's specifications and the JV3 Report; |  | Before COC |  | McNab
28 | Satisfactory final inspection certificate (Form 12) from the Fire Engineer stating compliance with the design requirements of the report; |  | Before COC |  | McNab
Part E - Appeal Rights
| The rights of an applicant to appeal to a tribunal or the Planning and Environment Court against a decision about a development application are set out in chapter 6, part 1 of the Planning Act 2016. For particular applications, there may also be a right to make an application for a declaration by a tribunal (see chapter 6, part 2 of the Planning Act 2016). |  | N/A
| Appeal by an Applicant An applicant for a development application may appeal to the Planning and Environment Court against the following: • the refusal of all or part of the development application • a provision of the development approval • the decision to give a preliminary approval when a development permit was applied for • a deemed refusal of the development application. An applicant may also have a right to appeal to the Development tribunal. For more information, see schedule 1 of thePlanning Act 2016. |  | N/A
| Appeal by a Submitter A submitter for a development application may appeal to the Planning and Environment Court against: • any part of the development application for the development approval that required impact assessment • a variation request. The timeframes for starting an appeal in the Planning and Environment Court are set out in section 229 of the Planning Act 2016 |  | N/A

## Data
RESPONSIBLE |  | TIMING
McNab |  | During Design
McNab & Rockpool |  | During Construction
McNab & GJG Architects |  | Before COC
McNab and Butler Webb
Rockpool | Client
GJG Architects | Architect
Butler & Webb | Landscape Designer
Aaction | Traffic Engineer
Cundall | Sustainabilty Certifier
ACOR Consultants | Structural Engineer
ACOR Consultants | Civil Engineer
ACOR Consultants | Hydraulic Engineer
STP Consultants | Fire Services Engineer
STP Consultants | Mechanical Services
STP Consultants | Electrical
McNab & STP | Building Certifier
Acoustic Engineer
STATUS
Outstanding
Complete
N/A
Progressing