## Slide 1: Apply Fire Protection Requirements
CPCCBC5001 - Apply building codes and standards to the construction process for Type B construction

## Slide 2: 3.1 Identify Passive and Active Fire Control Elements Required by Relevant Legislation
Apply Fire Protection Requirements
Before discussing fire safety systems, you must be able to determine the different classes of fire first. This will help you understand the hazards involved and identify the measures and equipment you have to use to contain each class of fire.
Fires are classified according to the materials that fuel them. A summary of fire classifications and their descriptions can be found below.

## Slide 3: 3.1 Identify Passive and Active Fire Control Elements Required by Relevant Legislation
Apply Fire Protection Requirements
Class A Fire
Involves carbonaceous solids (contains the chemical element carbon as the basic fuel) such as wood, paper, cloth, plastic, grass, coal or rubber
Class B Fire
Involves flammable liquids such as petrol, turpentine, kerosene, tar, paint or wax
Class C Fire
Involves flammable gases such as hydrogen, butane or methane
Class D Fire
Involves combustible metals such as sodium, magnesium, potassium or aluminum shavings

## Slide 4: 3.1 Identify Passive and Active Fire Control Elements Required by Relevant Legislation
Apply Fire Protection Requirements
The temperature of the oils that are on fire is higher than that of flammable liquids. Hence, normal extinguishing agents are ineffective.
Involves cooking fats and oils.
Class F Fire
Officially, there is no Class E fire because electricity is not a fuel. However, it is a source of heat and potential electric shock to a fire
Involves any of the materials found in Class A and B fires but with the introduction of electrical equipment such as wiring, electrical appliances and other electrically energised objects in the vicinity of the fire.
Electrical Fire
Once the electrical equipment is removed from the fire, the classification of fire changes.

## Slide 5: 3.1 Identify Passive and Active Fire Control Elements Required by Relevant Legislation
Apply Fire Protection Requirements
Fire safety systems refer to the means and equipment to detect, inform, intervene or evacuate a building when there is a fire. They typically perform one or a combination of the following functions:
Warn occupants when there is an emergency.
Ensure that the conditions for evacuation are safe.
Restrict the spread of fire to other parts of the building or adjoining buildings.
Suppress fire.
Fire safety systems are composed of both passive and active fire control elements that work together to protect a building from damage and its occupants from injury. These must be installed in buildings that are already in use and in buildings that are still undergoing construction.

## Slide 6: 3.1.1 Passive Fire Control Elements
Apply Fire Protection Requirements
Passive fire control elements involve the use of suitable materials (e.g. fire-resisting elements and fire doors) in the construction of a building to improve structural stability and reduce the likelihood of collapse. Unlike active fire control elements that aim to extinguish fire, passive fire control elements aim to contain the fire to its point of origin and prevent it from spreading to the other parts of the building.
This can be achieved through compartmentation, which is the process of breaking the building into areas of manageable risk. These areas are called ‘compartments’ which restrict the growth and spread of fire and smoke, making the fire easier to contain.
The next part will discuss examples of passive fire control elements and the functions that they play in fire protection.

## Slide 7: Fire-resisting building elements
Apply Fire Protection Requirements
Building materials, assemblies, linings and surface finishes must be able to resist the spread of fire and generation of smoke. The criteria for fire resistance are discussed in Section 3.2.

## Slide 8: Non-combustible building elements
Apply Fire Protection Requirements
These elements resist fire, provide compartmentation and restrict the spread of fire to ensure occupants' safety.

## Slide 9: Fire doors
Apply Fire Protection Requirements
These aim to protect openings by maintaining the integrity of fire separation and compartmentation. These include sliding fire doors, their associated warning systems and associated closing and latching mechanisms.
These may be made of a combination of materials such as glass, gypsum, steel or timber.

## Slide 10: Fire windows
Apply Fire Protection Requirements
These protect openings by maintaining the integrity of fire separation and compartmentation. Included are automatic or permanently fixed windows.

## Slide 11: Fire shutters
Apply Fire Protection Requirements
These provide fire separation and compartmentation by automatically closing when a fire is detected. Activation of shutters can be done either by connecting to the building’s fire alarm system or being fitted with their own heat detection system. Some shutters roll down under their weight. Other shutters are operated using a motorised closing mechanism.

## Slide 12: Smoke doors
Apply Fire Protection Requirements
These restrict the passage of smoke between compartments or walls. Included are associated self-closing, automatic closing and latching mechanisms.

## Slide 13: Proscenium walls (fire curtains)
Apply Fire Protection Requirements
These prevent the passage of smoke and fire from the stage area to the audience area in a theatre.

## Slide 14: 3.1.2 Active Fire Control Elements
Apply Fire Protection Requirements
Active fire control elements have a predetermined response to heat, smoke or specific gases. Some responses are automatic, such as turning sprinklers on and sounding the alarms. Others are manual, such as fire reel systems and portable fire extinguishers.
Active fire control elements can fall under two categories:
Elements to fight a fire in its early stages are simple and lightweight equipment to be used by the occupants to extinguish or contain a fire in its early stages. These are typically used while waiting for the fire brigade to arrive. Examples are fire hose reels and fire extinguishers.
Elements to assist the fire brigade are equipped to be used by the fire brigade. One example is a fire hydrant system.
The next part will discuss some examples of active fire control elements, their descriptions and the functions that they play in containing fire.

## Slide 15: Smoke and heat alarm and detection systems
Apply Fire Protection Requirements
These are installed to sense a fire in its initial development stage and warn building occupants.

## Slide 16: Fire hose reel systems
Apply Fire Protection Requirements
These consist of pumps, pipes, water supply and hose reels. These are placed in strategic locations throughout the building and are manually activated using a valve that enables water flow. They allow occupants to undertake initial fire extinguishment while waiting for the fire brigade.

## Slide 17: Portable fire extinguishers
Apply Fire Protection Requirements
Similar to fire hose reel systems, these allow occupants to undertake initial fire extinguishment while waiting for the fire brigade. These are located in strategic locations, often near a building's main exit and away from areas that are likely to catch fire. An example of a strategic placement would be placing a portable fire extinguisher at the kitchen entrance but not inside the kitchen.

## Slide 18: Portable fire extinguishers
Apply Fire Protection Requirements
No type of fire extinguisher can work on all classes of fire. This is why you must choose extinguishers with an extinguishing agent suitable to the class of fire that your building is prone to.
The five main types of fire extinguishers in Australia are identifiable by the colour of their bands. These are classified according to their extinguishing agent.

## Slide 19: Portable fire extinguishers
Apply Fire Protection Requirements
The table below shows the different types of extinguisher and the class of fire they are suitable for.
Type of Extinguisher | Suitable for (class of fire) | Comments
Water (identified by an all-red body; no band) | A | Not safe on other classes of fire Dangerous if used on flammable liquid, electrical equipment and cooking oil or lard fires
Foam (identified by a blue band) | A and B; F (limited effectiveness) | Not safe on other classes of fire Dangerous if used on energised electrical equipment

## Slide 20: Portable fire extinguishers
Apply Fire Protection Requirements
Type of Extinguisher | Suitable for (class of fire) | Comments
Dry Chemical Powder (identified by a white band) | An ABE unit is suitable for A, B, C and E fires A BE unit is suitable for B, C, E and F fires | Check the label carefully to determine if the fire extinguisher is a BE or ABE unit The ABE unit is ideal for most household fires
Wet Chemical (identified by an oatmeal band) | A and F | Dangerous if used on energised electrical equipment
Carbon Dioxide (CO2) (identified by a black band) | A and B (limited effectiveness); E | Not suitable for outdoor use or large class A fires

## Slide 21: Fire hydrant systems
Apply Fire Protection Requirements
Fire hydrant systems include an on-site pump set and fire service booster connection. These should only be installed in places with fire brigade access. Fire hydrants give the fire brigade access to the main water supply.

## Slide 22: Emergency Warning and Intercommunication Systems (EWIS) and Building Occupant Warning System
Apply Fire Protection Requirements
These are installed in a building to alert occupants and allow for a comprehensive and controlled evacuation during emergencies.

## Slide 23: Emergency lighting and exit signs
Apply Fire Protection Requirements
It prevents the occupants’ injury by providing sufficient light and signages during evacuation. All emergency lighting and exit signs must have their own alternative energy supply in case there is a failure in the main supply.
Previously, emergency exit signs used the word “EXIT.” The new updates in the AS now only allow the following pictograms as shown in the figures below:

## Slide 24: Automatic fire sprinkler systems
Apply Fire Protection Requirements
There are also known as wet pipe systems. These are installed into the ceiling and are activated when there is an increase in temperature. Once activated, the sprinklers will douse the area with a continuous supply of water until the system shuts off.

## Slide 25: Automatic fire sprinkler systems
Apply Fire Protection Requirements
Automatic fire sprinkler systems may include:
wet pipe systems and sprinklers
valve installations
electric motor and compression-ignition engines and pump sets
fire brigade booster connections
water storage systems
alarms and interface with automatic fire and detection systems

## Slide 26: Smoke and heat vents
Apply Fire Protection Requirements
These are openings installed on the roof to discharge smoke and heat generated by fire.

## Slide 27: 3.1.3 Legislation Relevant to Fire Safety Systems
Apply Fire Protection Requirements
Following legislation mandating fire safety systems installation is central to protecting the building and its occupants from the undesirable consequences of fire.
The table below shows acts and regulations to fire safety specific to certain states or territories. Note that the table below does not show all fire safety legislation in your state/territory; you should still conduct further research or consult with an Appropriate Authority to ensure that all relevant fire legislation requirements that apply to you are followed.

## Slide 28: 3.1.3 Legislation Relevant to Fire Safety Systems
Apply Fire Protection Requirements
State/Territory | Fire Safety Legislation
Australian Capital Territory | Building (General) Regulation 2008 Emergencies Act 2004
New South Wales | Environmental Planning and Assessment Regulations 2000
Northern Territory | Fire and Emergency Act 1996
Queensland | Building Fire Safety Regulation 2008
South Australia | Fire and Emergency Services Act 2005
Tasmania | General Fire Regulations 2010
Victoria | Building Act 1993 Building Regulations 2006
Western Australia | Fire and Emergency Services Act 1998

## Slide 29: 3.2.1 Fire Resistance Level
Apply Fire Protection Requirements
The fire resistance level (FRL) refers to the ability of a building or a building element to withstand fire under test conditions for a certain period. A building element that achieves the FRL appropriate for that element is considered a fire-resisting element.
AS/NZS 1530.4 covers methods for fire tests conducted on building materials, components and structures. These tests are conducted in a laboratory to determine the fire resistance of elements of construction.

## Slide 30: 3.2.1 Fire Resistance Level
Apply Fire Protection Requirements
In these tests, a representative sample of the element is subjected to tests and monitored based on the following criteria:
Structural adequacy refers to the ability to maintain stability and adequate loadbearing capacity (i.e. how long it would take for an element to collapse)
Integrity is the resistance to the passage of flames and hot gases (i.e. how long it would take an element to crack).
Insulation is the ability to maintain a certain temperature on the surface not exposed to the fire. The temperature must be kept below the specified limits in AS 1530.4 (i.e. how long it would take an element to heat on the other side of the fire to 220 degrees Celsius).

## Slide 31: 3.2.1 Fire Resistance Level
Apply Fire Protection Requirements
Fire resistance is expressed as the time for which the criteria have been satisfied. This is written in the order that they are presented above. For example, 120/30/30 is interpreted as the tested element having 120 minutes of structural adequacy, 30 minutes of integrity and 30 minutes of insulation. Sometimes, you will see a dash in place of a value, such as -/60/60. This means that only the integrity and insulation were tested for and there is no requirement for structural adequacy.

## Slide 32: 3.2.2 Required Type of Fire-resisting Construction
Apply Fire Protection Requirements
A fire-resisting building or structure must be provided with the FRL that the NCC specifies. To construct a fire-resisting building, you must use the minimum type of fire-resisting construction. Fire-resisting construction is based on building classifications and rise in storeys.
Before you can determine the type of fire-resisting construction needed for your building, you must first learn how to calculate storeys. A storey refers to the space within a building that is situated between one floor level and the floor level above it. If there is no floor above it, the ceiling or roof above will be counted.

## Slide 33: 3.2.2 Required Type of Fire-resisting Construction
Apply Fire Protection Requirements
However, the ceiling or roof will not be counted if it contains only the following:
sanitary compartments such as a bathroom, shower room, or laundry room
a lift shaft, stairway, or meter room
maintenance equipment such as air conditioning units
accommodation intended for more than three vehicles
mezzanine
For example, a building has three floors, but the third floor only contains a mezzanine. This means that this building only has two storeys given the condition above.

## Slide 34: 3.2.2 Required Type of Fire-resisting Construction
Apply Fire Protection Requirements
Now that you have calculated the rise in storeys, you may refer to the table below to determine the minimum type of construction required for your building:
Rise in Storeys | Class of Building 2, 3, 9 | Class of Building 5, 6, 7, 8
4 or more | A | A
3 | A | B
2 | B | C
1 | C | C

## Slide 35: 3.2.2 Required Type of Fire-resisting Construction
Apply Fire Protection Requirements
Buildings classified as class 2, 3 and 9 with a maximum of two storeys require type B construction.
Buildings classified as class 5, 6, 7 and 8 with a maximum of three storeys require type B construction.
In terms of fire-resistance, Type B construction falls somewhere in between Type A which is the most fire-resistant and Type C which is the least fire-resistant.

## Slide 36: 3.3 Apply NCC Requirements with Respect to Passive and Active Fire Protection to Buildings up to Three Storeys
Apply Fire Protection Requirements
The purpose of fire safety systems is to stop or slow the spread of flames and smoke in a fire, allowing fire personnel to safely access the building during a fire. If a building is not designed with the appropriate elements, it may collapse and put people at risk.
In the next part, the requirements specified by the NCC regarding both passive and active fire protection requirements will be discussed. Relevant Australian Standards will also be identified. Note that other applicable AS and NCC requirements may not have been mentioned. As such, it is recommended that you look them up or consult with an Appropriate Authority to check which applies to your building.

## Slide 37: 3.3.1 Passive Fire Protection Requirements
Apply Fire Protection Requirements
As mentioned earlier, passive fire protection measures typically refer to the components and materials that help maintain the structural fire protection of a building. The table below summarises the NCC requirements of passive fire protection elements and the respective Australian Standards.

## Slide 38: 3.3.1 Passive Fire Protection Requirements
Apply Fire Protection Requirements
Passive Fire Protection | NCC Requirements | Relevant Australian Standards
Fire-resisting building elements | Must be constructed entirely of non-combustible materials subject to AS 1530.1 - Combustibility Tests for Materials Must be designed to achieve the fire-resistance level according to the relevant AS | AS/NZS 2327, AS 4100 and AS/NZS 4600 if it is a steel or composite structure AS 3600 if it is a concrete structure AS 1720.4 if it is a timber element other than fire-protected timber AS 3700 if it is a masonry structure

## Slide 39: 3.3.1 Passive Fire Protection Requirements
Apply Fire Protection Requirements
Passive Fire Protection | NCC Requirements | Relevant Australian Standards
Non-combustible building elements | In a type B construction, the following elements must be non-combustible: external walls and common walls, including all incorporated components such as façade framing and insulation flooring and floor framing shaft (applicable if the shaft is non-loadbearing and not used for discharging hot products) | AS 1530.4

## Slide 40: 3.3.1 Passive Fire Protection Requirements
Apply Fire Protection Requirements
Passive Fire Protection | NCC Requirements | Relevant Australian Standards
 | Examples of non-combustible materials, according to NCC are: plasterboard perforated gypsum lath with a normal paper finish fibrous-plaster sheet fibre-reinforced cement sheeting | 

## Slide 41: 3.3.1 Passive Fire Protection Requirements
Apply Fire Protection Requirements
Passive Fire Protection | NCC Requirements | Relevant Australian Standards
Fire doors | Must be able to fulfil all relevant test requirements Must be self-closing which means that the door must fully close immediately every time it is opened Must automatically close when the sensor is triggered or when power supply is lost Must have latch sets and closers marked as required Must have a metal tag attached as required by AS 1905.1 | AS 1905.1

## Slide 42: 3.3.1 Passive Fire Protection Requirements
Apply Fire Protection Requirements
Passive Fire Protection | NCC Requirements | Relevant Australian Standards
Fire windows | Must be constructed and installed identical to a tested an approved prototype | AS 1530.4
Fire shutters | Must be constructed and installed identical to a tested an approved prototype Must operate automatically and close at a rate of 0.25 to 0.3 meters per second Must maintain integrity as required | AS 1905.2

## Slide 43: 3.3.1 Passive Fire Protection Requirements
Apply Fire Protection Requirements
Passive Fire Protection | NCC Requirements | Relevant Australian Standards
Smoke doors | Smoke should not pass through from one side of the doorway to the other end. If the smoke door is glazed, danger of a person accidentally walking into it must be minimised. Smoke doors can be one or two leaves and must: swing in the direction of egress or both directions resist smoke at 300 degree Celsius for 30 minutes have leaves fitted with smoke seals | AS 6905-2007

## Slide 44: 3.3.1 Passive Fire Protection Requirements
Apply Fire Protection Requirements
Passive Fire Protection | NCC Requirements | Relevant Australian Standards
Proscenium walls (fire curtains) | Made of non-combustible material Must stop penetration of smoke around the perimeter when fully lowered | 

## Slide 45: 3.3.2 Active Fire Protection Requirements
Apply Fire Protection Requirements
On the other hand, active fire protection is the use of firefighting techniques and equipment to fight the source of a fire and extinguish it. The table below shows active fire protection elements with their respective NCC requirements and Australian Standards.

## Slide 46: 3.3.2 Active Fire Protection Requirements
Apply Fire Protection Requirements
Active Fire Protection | NCC Requirements | Relevant Australian Standards
Smoke and heat alarm systems | Must be able to sense the presence of a fire and identify its location Must advise the fire brigade if required Must be in a building where sprinklers are not installed Must be connected to a building occupant warning system In places like the kitchen where there is a lot of smoke that can confuse a smoke alarm system, you are advised to install a heat alarm instead | AS 3786

## Slide 47: 3.3.2 Active Fire Protection Requirements
Apply Fire Protection Requirements
Active Fire Protection | NCC Requirements | Relevant Australian Standards
Smoke and Heat Detection Systems | Must be able to sense the presence of a fire and identify its location Must advise the fire brigade if required Must be able to switch air handling system into smoke ventilating mode Must close smoke and fire-isolating doors as necessary Must activate necessary fire pumps In places like the kitchen where there is a lot of smoke that can confuse a smoke alarm system, you are advised to install a heat alarm instead | AS 1670

## Slide 48: 3.3.2 Active Fire Protection Requirements
Apply Fire Protection Requirements
Active Fire Protection | NCC Requirements | Relevant Australian Standards
Fire hose reel systems | Must be long enough to reach every floor or storey where it is installed by laying the hose along normal lines of access For 19 mm hoses, there must be a water supply rate of at least 0.33 litres/second For 25 mm hoses, there must be a water supply rate of at least 0.41 litres/second | AS 2441
Portable fire extinguishers | Must be marked with the class and size of fire for which they have been successfully tested Must be located in conspicuous and accessible locations Locations must have appropriate signage | AS 1850 AS 2444

## Slide 49: 3.3.2 Active Fire Protection Requirements
Apply Fire Protection Requirements
Active Fire Protection | NCC Requirements | Relevant Australian Standards
Fire hydrants | Must be installed according to AS 2419.1 Must be located to provide coverage to every part of the building or site that requires coverage Must meet the required minimum flow of water at all times Must be readily accessible to firefighting personnel | AS 2419.1
Emergency warning and intercom systems | Must have the following facilities: a master emergency control panel (MECP) any necessary additional emergency control panels (ECP) necessary distribution system to transmit a warning signal to each evacuation zone | AS 1670.4

## Slide 50: 3.3.2 Active Fire Protection Requirements
Apply Fire Protection Requirements
Active Fire Protection | NCC Requirements | Relevant Australian Standards
 | a warden intercommunication point (WIP) on each floor or in each evacuation zone a notice at each ECP with clear instructions on how to operate them an interconnection with the building fire alarm system | 
Building Occupant Warning System | Must have a sound system for an emergency that is triggered by the fire-detection system Must have electronic sounders or amplified sound systems that produce an evacuation signal Evacuation signal must operate simultaneously throughout the building | AS 1670.4

## Slide 51: 3.3.2 Active Fire Protection Requirements
Apply Fire Protection Requirements
Active Fire Protection | NCC Requirements | Relevant Australian Standards
Emergency escape lighting and signs | Be installed according to AS 2993.1 Automatically operate when there is power supply failure in the main lighting system Luminance must be appropriate to: the use and size in the floor area of the building the distance to the exits | AS 2293.1
Automatic fire sprinkler systems | Must comply with AS 2118 Must be maintained in accordance with AS 1851-2005 Section 2 | AS 2118.1 AS 2118.4 AS 2118.6

## Slide 52: 3.3.2 Active Fire Protection Requirements
Apply Fire Protection Requirements
Active Fire Protection | NCC Requirements | Relevant Australian Standards
Smoke and heat vents | Must have the following components: vents and their operating mechanism draught curtains inlet ventilation | AS 2665

## Slide 53: 3.3.2 Active Fire Protection Requirements
Apply Fire Protection Requirements
Aside from the relevant AS for the fire protection elements, there are also other AS that are specific to buildings that need a higher degree of fire protection. These are commonly buildings located in areas with greater risk of fires.

## Slide 54: 3.3.2 Active Fire Protection Requirements
Apply Fire Protection Requirements
An example is the AS 3959 which covers the safety requirements of buildings in bushfire-prone areas. The requirements that you have to comply with depend on the Bushfire Attack Level (BAL), which refers to the measure of the severity of a building’s exposure to ember attack, radiant heat and direct flame contact. BAL is measured in increments of radiant heat. The following are the six categories of BAL:
BAL Low
BAL 12.5
BAL 19
BAL 29
BAL 40
BAL Flame Zone
Construction measures range from ember protection at the lowest level to direct flame protection at the highest level.

## Slide 55: 3.4 Check Passive and Active Fire Protection Requirements are Applied during and on Completion of Works
Apply Fire Protection Requirements
Fire protection requirements must be applied not just to completed buildings, but to buildings under construction as well. This is because construction sites are particularly prone to fire because of activities such as:
Soldering, welding and brazing
Thermal spraying
Cutting
Grinding steel
Using a blow torch
Installing heat-applied materials
You have the responsibility to ensure that fire protection requirements are provided and installed. You must also check that each requirement works properly and as designed.

## Slide 56: 3.4 Check Passive and Active Fire Protection Requirements are Applied during and on Completion of Works
Apply Fire Protection Requirements
To do this, you must conduct the following activities during and on completion of building works:
Install an effective fire alarm system. Test to make sure that the sensors and sirens are working. If the sound is weak or non-existent, replace the batteries.
Check that all fire protection equipment are positioned appropriately. Ensure that there are clear signages to point occupants to their location.
Conduct checks to ensure that electrical appliances, equipment and machinery are in safe condition. Make sure that there are no exposed wirings.
Keep sprinkler heads free from obstruction. The sprinklers should meet the required water flow and pressure.

## Slide 57: 3.4 Check Passive and Active Fire Protection Requirements are Applied during and on Completion of Works
Apply Fire Protection Requirements
Electrical circuits and extension cords should not be overloaded. Turn off machinery and equipment when not in use to prevent electrical fire.
Keep evacuation routes free from obstruction (e.g. debris and construction materials).
During construction, there must be at least one fire extinguisher for Class A, B and C fires and electrical fires on each storey adjacent to each required exit or temporary stairway or exit. (See: E1.9 of the NCC)
During construction, a building that reached a height of 12m must have operational fire hydrants and fire hose reels in at least every storey (except the two uppermost storeys). Any required booster connections must be installed. (See: E1.9 of the NCC)

## Slide 58: What have we learned?
In this part of the session, we have covered:
Classify Buildings
Determine Compliance Solutions within the NCC
Apply Fire Protection Requirements

## Slide 59
End of Part 3

## Slide 60: Presentation Objectives
Now that you have completed this presentation, you should be able to:
Classify Buildings
Determine Compliance Solutions within the NCC
Apply Fire Protection Requirements

## Slide 61
End of CPCCBC5001 Presentation