## SECURE
QBTS: Building Certification Checklist - Internal Monitoring -SECURE | [5 empty] | Updated 08.01.2025
No. | Item | S12 | S34 | S56 | E2 | DU | TH1 | TH2 | COLOUR LEGEND
Inspection Building Checkpoints
1 | Fire Source Feature Plan | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | QBTS - 08/01 - Softcopy to be issued on Aconex | QBTS - 06/02- Softcopy to be issued on Aconex | QBTS - 11/02- Softcopy to be issued on Aconex |  | Item Closed Onsite JHG to Issue Supporting Documentation
2 | Fire Penetration Register in accordance with AS4072.1 | Rectified Onsite - Pending Issue of Register to QBTS | Rectified Onsite - Pending Issue of Register to QBTS | Rectified Onsite - Pending Issue of Register to QBTS | QBuil-GCOR-017842 - Accepted 05/03 | QBTS - 08/01 - Softcopy to be issued on Aconex | QBTS - 06/02- Softcopy to be issued on Aconex | Fredon - Penetrations Unsealed and Labelled |  | Oustanding Action
3 | Passive Fire Rating Labels in accordance with AS4072.1 | 03/12 - QBTS | 03/12 - QBTS - Confirm extent of tags against cross referenced registers | QBTS - 03/12- Softcopy to be issued on Aconex | QBTS - 08/01 | Accepted QBTS 26/02 - QBUIL-GCOR-017706 | Penetration - D-T12.17-B Additional Sealant Required | QBTS - 11/02- Softcopy to be issued on Aconex |  | Item Closed Out Rectification Issued on Aconex Pending QBTS Confirmation or Response
4 | Fire Rated Door suites (Doors & Frames) Certified & Labelled | JH-GCOR-077646 - Smoke Seals Installed - Issued to QBTS with Photos | JH-GCOR-077648 - Smoke Seals Installed - Issued to QBTS with Photos | Confirmed Ready Onsite - Waiting for QBTS Report | QBuil-GCOR-017842 - Accepted 05/03 | Smoke Seals and Fire Tags Installed -QBTS Approved QBUIL-GCOR-017706 | QBuil-GCOR-017850 - Accepted 05/03 | QBuil-GCOR-017852 - Accepted 06/03 |  | Closed Out and Approved by QBTS
5 | Passive Fire Protection to Structural Elements (E.g. Intumescent Paint) | 03/12 - QBTS- TR to resend to Scott Rubie | 03/12 - QBTS- TR to resend to Scott Rubie | 03/12 - QBTS- TR to resend to Scott Rubie | N/A | N/A | QBTS - 06/02 | QBTS - 11/02- Softcopy to be issued on Aconex |  | Not Applicable to this Building
6 | Certificates as per JH-7515-SCH-DCH-000001 | On Going | On Going | On Going | On Going | On Going | On Going | On Going |  | JHG Confirmed Ready Awaiting on Review Comments from QBTS
7 | DDA Bathroom Falls in accordance with AS1428.1 (Cl. 15) | MFP To Provide Form 12 For Rectified Falls | MFP To Provide Form 12 For Rectified Falls | 17/08 - QBTS | MFP To Provide Form 12 For Rectified Falls | MFP To Provide Form 12 For Rectified Falls | MFP To Provide Form 12 For Rectified Falls | MFP To Provide Form 12 For Rectified Falls |  | Item not Inspected by QBTS
8 | DDA handrails & Balustrades in accordance with AS1428.1 (Cl. 14) | 03/12 - QBTS | 03/12 - QBTS | 17/08 - QBTS | N/A | N/A | QBTS - 06/02 | Welded Joins on Balustrades Sharp - East Coast to Recitfy
9 | DDA- bathroom Cloths Hooks, Grabrails, Pans etc in accordance with AS1428.1 (Cl. 14) | 17/08 - QBTS Coat Hooks Approved JH-GCOR-077648 | 17/08 - QBTS 03/12- Coat Hooks MGC-CADV-000052 | 17/08 - QBTS 03/12- Coat Hooks MGC-CADV-000052 | QBTS - 28.02 QBUIL-GCOR-017756 and QBuil-GCOR-017695 | Backrest Loose- JH-GCOR-078399 - ASSA Vistor PWD Signage to be Rectifified JHG-GCOR-075860 | QBTS - 06/02 | Rail sitting 10mm to low (not Fixed) 10mm to High
10 | Placement of Light Switches in accordance with AS1428.1 (Cl. 14) | IP Rated Switches - Chase Documentation from Fredon to show switchover completed | IP Rated Switches - Chase Documentation from Fredon to show switchover completed | IP Rated Switches - Chase Documentation from Fredon to show switchover completed | QBTS - 08/01 | QBTS - 08/01 - Issue Exemption | IP Rated Switches - Chase Documentation from Fredon to show switchover completed | IP Rated Switches - Chase Documentation from Fredon to show switchover completed
11 | Placement of Break Glass Units in accordance with AS1428.1 (Cl. 13) | Pending Functionailty Testing - With Commissioning (Services Team)- Send Note to SR confirming completion | Pending Functionailty Testing - With Commissioning (Services Team)- Send Note to SR confirming completion | Pending Functionailty Testing - With Commissioning (Services Team)- Send Note to SR confirming completion | QBTS - 08/01 | Plant Room - Stair 1 No Break Glass At Base of Stair- Check Onsite | Labelling Missing from Break Glass Units- JH-GCOR-078371 | QBTS - 11/02
12 | Glazing decals/ Visual indicators in accordance with AS1428.1 (CL6.6) | N/A - No Frameless or Fully Glazed Doors | N/A - No Frameless or Fully Glazed Doors | N/A - No Frameless or Fully Glazed Doors | QBTS - 08/01 | N/A - No Frameless or Fully Glazed Doors | N/A - No Frameless or Fully Glazed Doors | N/A - No Frameless or Fully Glazed Doors
13 | Door Forces to not exceed 20N in accordance with AS1428.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
14 | Latch side clearance (530mm MIN) in accordance with AS1428.1 | 17/08 - QBTS | 03/12 QBTS - Cell S3.36,33,25 Slighly out confirm mckenzie advice | 03/03- QBTS | QBTS - 08/01 | QBTS - 08/01 | QBTS - 06/02 | QBTS - 11/02
15 | Installation of Emergency Egress Path Signage | 03/12 QBTS | 03/12 QBTS | 03/03- QBTS (Installation Done pending labels application) | QBTS - 20/03 - Accepted Modifications | QBTS -26/02 QBUIL-GCOR-017706 | Exit Signage - Installation Height outside L1 Switchroom Installed Below 2m Height Minimum | QBTS - 11/02
16 | Installation of Block Plan Signage - Sprinkler Valve Cupboards Only | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03
17 | Installation of Fire Extinguishers & associated Extinguisher Signage | FHR Drum Location Adjustment Required | FHR Drum Location Adjustment Required | FHR Drum Location Adjustment Required | Maitenance Stickers to ER3.32A and ER3.31 | Stabilisation of FHR - Supporting Pole Sways when Hose is extracted - AZ to issue advice | FHR Drum Location Adjustment Required | FHR- 100mm clearance around Hose Reel not achieved and Cages Missing from Sprinklers
18 | Installation of HAZARD TAPE on equipment <2.1m within plantroom spaces | QBuil-GCOR-018015 - Accepted 19/03 | 03/12 QBTS | 03/12 QBTS | N/A | JH-GCOR-078491 - 14/03 | 18/02 - Confirmed Completed on site with Low Head Height Sign Applied | Additional Hazard Tape to Be Applied and Bolts to Be Sheared Down and Stepdown Painted
19 | Emergency Lighting Test register present at Switchboard & adequate LUX levels in accordance with AS2293. | Completed Defect Free | Completed Defect Free | Completed Defect Free | Completed Defect Free | Inspected Awaiting Defects Closeout | Completed Defect Free | Completed Defect Free
20 | Emergency Eye Wash / Shower Maintenance register | N/A | N/A | N/A | N/A | N/A | N/A | N/A
21 | General Stairs: Rise & Going Compliance | 17/08- QBTS Form 12 Attached | 03/12 QBTS | 17/08- Form12 S6 Stair 2 Goings- 10/09 Steel Dayroom Pass | N/A | N/A | QBTS - 06/02- Softcopy to be issued on Aconex | Ready for QBTS - JHG Confirmed
22 | Plantroom Stairs: Rise & Going Compliance- Issue all Form12s | 17/08- QBTS Form 12 Attached | 03/12 QBTS | 17/08 - QBTS with Form12 - 10/09 Concrete Plant Pass | N/A | Issue Form 12 to SR | QBTS - 06/02- Softcopy to be issued on Aconex | 50mm Clearance Zone to Reticulation Zone Ladder Issued to QBTS 27.02
23 | Ramp Fall Compliance | N/A | N/A | N/A | N/A | N/A | N/A | N/A
24 | Threshold Compliance | JH-GCOR-077648 | Rectified Onsite - Pending Issue of Form 12 to Aconex. | Rectified Onsite - Pending Issue of Form 12 to Aconex. | Rectified Onsite - Pending Issue of Form 12 to Aconex. | Rectified Onsite - Pending Issue of Form 12 to Aconex. | Rectified Onsite - Pending Issue of Form 12 to Aconex. | Rectified Onsite - Pending Issue of Form 12 to Aconex.
25 | Tactiles | N/A -[ GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858]
26 | Catwalks / suspended platform compliance | QBuil-GCOR-017843 - Accepted 05/03 | QBuil-GCOR-017844 - Accepted 05/03 | QBuil-GCOR-017848 - Accepted 05/03 | N/A | QBTS Approved 24/03 - QBUIL-GCOR-018098 | QBuil-GCOR-017850 - Accepted 05/03 | QBuil-GCOR-017852 - Accepted 06/03
27 | Roof Safety System Compliance | Certificates - Uploaded on Aconex | Certificates - Uploaded on Aconex | Certificates - Uploaded on Aconex | Certificates - Uploaded on Aconex | Certificates - Uploaded on Aconex | Certificates - Uploaded on Aconex | Certificates - Uploaded on Aconex
Witness Testing Points
1 | Fire Detection Witness Test | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items |  |  | Scheduled for 21/01/2025 | TBC
2 | EWIS SPL Testing & Strobe activation | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items |  |  | Scheduled for 21/01/2025
3 | IST (Integrated Systems Test) Testing of Life Safety Services – E.g. HVAC Fire Matrix & Fire or Gas & Fire | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items |  |  | Scheduled for 21/01/2025
4 | Wet Fire Systems: Purge & Deluge Testing | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items |  |  | Scheduled for 21/01/2025
5 | Response Times inline with FER | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage

## RESIDENTIAL
QBTS: Building Certification Checklist - Internal Monitoring - RESIDENTIAL
No. | Item | T1 (R10) | T2 (R11) | T3 (R12) | T4 (R13) | R5 | R6 | R7 | R8 | R9 | ER (E1) | R4 | R3 | R1 | R2 | X22
| Inspection Building Checkpoints | [15 empty] | COLOUR LEGEND
1 | Fire Source Feature Plan | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval
2 | Fire Penetration Register in accordance with AS4072.1 | QBTS - 10/12 Issue Softcopy on Aconex | QBTS - 10/12 Issue Softcopy on Aconex | QBTS - 10/12 Issue Softcopy on Aconex | QBTS - 10/12 Issue Softcopy on Aconex | Fredon and BSA Penetrations not Sealed - JH-GCOR-077212 | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 10/12 Issue Softcopy on Aconex | QBTS - 10/12 Issue Softcopy on Aconex | QBTS - 10/12 Issue Softcopy on Aconex | QBTS - 10/12 | Rectified 14/02- SER West Upper Wall large penetration not labelled | QBTS - 20/01 Issue Softcopy on Aconex | QBTS - 20/01 Issue Softcopy on Aconex | QBTS - 20/01 Issue Softcopy on Aconex | Ready for QBTS - JHG Confirmed |  | Item Closed Onsite JHG to Issue Supporting Documentation
3 | Passive Fire Rating Labels in accordance with AS4072.1 | QBTS-10/12 - Accepted Onsite Documentation to be provided on Aconex | QBTS-10/12 - Accepted Onsite Documentation to be provided on Aconex | QBTS-10/12 - Accepted Onsite Documentation to be provided on Aconex | QBTS-10/12 - Accepted Onsite Documentation to be provided on Aconex | JH-GCOR-077212 | QBTS-10/12 - Accepted Onsite Documentation to be provided on Aconex | QBTS-10/12 - Accepted Onsite Documentation to be provided on Aconex | QBTS-10/12 - Accepted Onsite Documentation to be provided on Aconex | QBTS-10/12 - Accepted Onsite Documentation to be provided on Aconex | QBTS-10/12 - Accepted Onsite Documentation to be provided on Aconex | Rectified 14/02- SER West Upper Wall large penetration not labelled | QBTS-20/01- Accepted Onsite Documentation to be provided on Aconex | QBTS-20/01- Accepted Onsite Documentation to be provided on Aconex | QBTS-20/01- Accepted Onsite Documentation to be provided on Aconex |  |  | Oustanding Action
4 | Fire Rated Door suites (Doors & Frames) Certified & Labelled | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 19/02 | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 20/01 Issue Softcopy on Aconex | QBTS - 20/01 Issue Softcopy on Aconex | QBTS - 20/01 Issue Softcopy on Aconex | QBTS - 20/01 Issue Softcopy on Aconex |  |  | Item Closed Out Rectification Issued on Aconex Pending QBTS Confirmation or Response
5 | Passive Fire Protection to Structural Elements (E.g. Intumescent Paint) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Closed Out and Approved by QBTS
6 | Certificates as per JH-7515-SCH-DCH-000001 | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Final Packs to be issued with all documentation | Issue on Aconex |  | Not Applicable to this Building
7 | DDA Bathroom Falls in accordance with AS1428.1 (Cl. 15) | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 | Form 12 Received to Be Provided in Final Certification Packs - MFP GCOR-000500 |  |  | JHG Confirmed Ready Awaiting on Review Comments from QBTS
8 | DDA handrails & Balustrades in accordance with AS1428.1 (Cl. 14) | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 19/02 | QBTS - 20/01 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01 |  |  | Item not Inspected by QBTS
9 | DDA- bathroom Cloths Hooks, Grabrails, Pans etc in accordance with AS1428.1 (Cl. 14) | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 19/02 | QBTS - 20/01 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 20/01 | QBTS - 20/01 | 20/01- Wing A PWD Toilet Handrail Sitting at 790mm - Rectified | QBTS - 20/01
10 | Placement of Light Switches in accordance with AS1428.1 (Cl. 14) | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 19/02 | QBTS - 20/01 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01
11 | Placement of Break Glass Units in accordance with AS1428.1 (Cl. 13) | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | Placement Okay - Pending Labelling 19/02 | QBTS - 20/01 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01
12 | Glazing decals/ Visual indicators in accordance with AS1428.1 (CL6.6) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
13 | Door Forces to not exceed 20N in accordance with AS1428.1 | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment | To Be Completed - JHG to obtain pull test equipment
14 | Latch side clearance (530mm MIN) in accordance with AS1428.1 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | JH-GCOR-078095 John Barnes PWD Free Escape not in place when door is snibbed | QBTS - 20/01 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01
15 | Installation of Emergency Egress Path Signage | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | JH-GCOR-077212 | QBTS - 20/01 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01
16 | Installation of Block Plan Signage | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03
17 | Installation of Fire Extinguishers & associated Extinguisher Signage | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 19/02 | QBTS - 20/01 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | 10/12 - Check FE Cupboards (ER3.32A and ER1) Signed for FE but only hose inside - Ready 16/02 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01 | QBTS - 20/01
18 | Installation of HAZARD TAPE on equipment <2.1m within plantroom spaces | QBTS - QBUIL-GCOR-018014 Accepted 19/03 | QBTS - QBUIL-GCOR-0127970 Accepted | QBTS - QBUIL-GCOR-017972 Accepted | JH-GCOR-078146 - 05/03 | Bolts Capped - 20/03 JH-GCOR-078722 | Capped Bolts 18/03 - JH-GCOR-0078587 | Capped Bolts - 05/03 JH-GCOR-078138 | QBuil-GCOR-018016 - Accepted 19/03 | QBTS - 10/12 | N/A | QBuil-GCOR-018018 - Accepted 19/03 | QBuil-GCOR-018017 - Accepted 19/03 | QBuil-GCOR-018018 - Accepted 19/03 | Low Headheight Bolts Capped - JH-GCOR-078725
19 | Emergency Lighting Test register present at Switchboard & adequate LUX levels in accordance with AS2293. | Completed Defect Free | Completed Defect Free | Completed Defect Free | Completed Defect Free | Completed Defect Free | Completed Defect Free | Completed Defect Free | Completed Defect Free | Completed Defect Free | Inspected Awaiting Defects Closeout | Completed Defect Free | Completed Defect Free | Completed Defect Free | Completed Defect Free
20 | Emergency Eye Wash / Shower Maintenance register | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
21 | General Stairs: Rise & Going Compliance | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 19/02 | QBTS - 20/01 Issue Form 12 Aconex | Ready for QBTS- JHG Confirmed - Stair Nosing Applied | Ready for QBTS- JHG Confirmed - Stair Nosing Applied | QBTS - 10/12 | N/A | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex
22 | Plantroom Stairs: Rise & Going Compliance | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
23 | Ramp Fall Compliance | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
24 | Threshold Compliance | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 10/12 | QBTS - 19/02 | QBTS - 20/01 | Wing A - Threshold Not Compliant 220/32 | QBTS - 10/12 | QBTS - 10/12 | Threshold Rectifications - Actioned | Wing B - 35 H 220L - Non Compliant | Wing A & B - Non Compliant | QBTS - 20/01 | QBTS - 20/01
25 | Tactiles | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858]
26 | Catwalks / suspended platform compliance | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
27 | Roof Safety System Compliance | EWP Screws Plate - Issued 24/02 Aconex | EWP Screws Plate - Issued 24/02 Aconex | EWP Screws Plate - Issued 24/02 Aconex | EWP Screws Plate - Issued 24/02 Aconex | QBTS - 19/02 | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex | QBTS - 20/01 Issue Form 12 Aconex
Witness Testing Points
1 | Fire Detection Witness Test | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items
2 | EWIS SPL Testing & Strobe activation | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items
3 | IST (Integrated Systems Test) Testing of Life Safety Services – E.g. HVAC Fire Matrix & Fire or Gas & Fire | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items
4 | Wet Fire Systems: Purge & Deluge Testing | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items
5 | Response Times inline with FER | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage

## SUPPORT
QBTS: Building Certification Checklist - Internal Monitoring - SUPPORT | [7 empty] | APPROVED ONSITE 27/03
No. | Item | X21 | GH | AD | Y | MU | PP | Q | KL | IN | H1 | H2 | X23 | VP | VI
| Inspection Building Checkpoints | [14 empty] | COLOUR LEGEND
1 | Fire Source Feature Plan | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | N/A | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Awaiting State Approval | Documentation Issued on Aconex JH-TRANSMIT-007881 | Awaiting State Approval | Awaiting State Approval
2 | Fire Penetration Register in accordance with AS4072.1 | Ready for QBTS - JHG Confirmed | QBTS -05/02- Softcopy to be issued on Aconex | QBTS- 21/03 | QBuil-GCOR-017853 - Accepted 06/03 | QBTS - 08/01 - Softcopy to be issued on Aconex | QBTS - 08/01 - Softcopy to be issued on Aconex | QBTS - 07/01 - Softcopy to be issued on Aconex | QBTS - 06/02 - Softcopy to be issued on Aconex | W.04 Axis Missing Labels to High Level Penetation - JH-GCOR-078827 | Penetrations to SER Room - Penetrations Above SER Door- Covered in BJS Statement JH-GCOR-078809 | QBTS - 08/01 | Documentation Issued on Aconex JH-TRANSMIT-007881 | JH-GCOR-078762 - Disputed Fire Rating of Electrical Room to X1 | QBTS - 21/03 |  | Item Closed Onsite JHG to Issue Supporting Documentation
3 | Passive Fire Rating Labels in accordance with AS4072.1 | Check Onsite | SER Comms& SEC - Trays Actioned JH-GCOR-078663 Remaining Items - Flexi Conduit and GH Plant Room Remaining | Labelling of Devices - Mail Sorting Room | QBTS - 10/01 | QBTS - 08/01 | QBTS - 08/01 | N/A | QBTS - 06/02 - Softcopy to be issued on Aconex | QBTS - 21/03 | QBTS - 08/01 | QBuil-GCOR-017840 - Accepted | Documentation Issued on Aconex JH-TRANSMIT-007881 |  | RFI Raised - Fire Sprinklers Sitting Above base of acoustic fin - Family Visits- JH-RFI-005653 |  | Oustanding Action
4 | Fire Rated Door suites (Doors & Frames) Certified & Labelled | Check Onsite | Doors Okay - QBTS 05.02 MCR Window Requires Drenchers - Query Sitting with GBA WSP JH-GCOR-077878 | QBTS- 21/03 | JHG issue out updated fire door exemption table from Fire Engineer - Still in Development WSP ANZ-GCOR-005968 | JHG issue out updated fire door exemption table from Fire Engineer - Still in Development WSP ANZ-GCOR-005968 | QBTS - 08/01 | N/A | JHG issue out updated fire door exemption table from Fire Engineer - Still in Development WSP ANZ-GCOR-005968 | D-W.46-A - Door Frame to SER not core filled JH-GCOR-078827 | N/A | N/A | N/A Fire Doors Changed to Secure | QBTS - 21/03 | QBTS - 21/03 |  | Item Closed Out Rectification Issued on Aconex Pending QBTS Confirmation or Response
5 | Passive Fire Protection to Structural Elements (E.g. Intumescent Paint) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Closed Out and Approved by QBTS
6 | Certificates as per JH-7515-SCH-DCH-000001 | Issue on Aconex | Issue on Aconex | Issue on Aconex | Issue on Aconex | Issue on Aconex | Issue on Aconex | Issue on Aconex | Issue on Aconex | Issue on Aconex | Issue on Aconex | Issue on Aconex | Completed Defect Free | Issue on Aconex | Issue on Aconex |  | Not Applicable to this Building
7 | DDA Bathroom Falls in accordance with AS1428.1 (Cl. 15) | N/A | N/A - No DDA Shower | N/A - No DDA Shower | JHG- Ready for QBTS 07/01 | JHG- Ready for QBTS 07/01 | JHG- Ready for QBTS 07/01 | 27/03 QBTS | N/A | QBTS - 19/02 | QBTS - 08/01 | N/A | N/A | QBTS - 21/03 | QBTS - 21/03 |  | JHG Confirmed Ready Awaiting on Review Comments from QBTS
8 | DDA handrails & Balustrades in accordance with AS1428.1 (Cl. 14) | N/A | QBTS -05/02 | N/A | N/A | QBTS - 08/01 | QBTS - 08/01 | QBTS - 07/01 | QBTS - 06/02 | QBTS - 19/02 | QBTS - 08/01 | QBTS 19.02 | N/A | QBTS - 21/03 Existing | QBTS - 21/03 |  | Item not Inspected by QBTS
9 | DDA- bathroom Cloths Hooks, Grabrails, Pans etc in accordance with AS1428.1 (Cl. 14) | N/A | 26/02 QBUIL-GCOR-017757 | QBTS 24/06 | Ready for QBTS - JHG Confirmed - 28/01 Coat Hooks Installed | QBTS - 25/02 JH-GCOR-075716 | QBTS - 08/01 | 27/03 QBTS | QBTS - 06/02 | QBTS - 19/02 | QBTS - 03/03/25 - QBuil-GCOR-017780 | PWD Door Latch on Backwards | QBTS - 27.02.24 QBUIL-GCOR-017747 | QBTS - 21/03 Existing | QBTS - 21/03
10 | Placement of Light Switches in accordance with AS1428.1 (Cl. 14) |  | QBTS -05/02 | QBTS 24/06 | QBTS - 10/01 | QBTS - 08/01 | QBTS - 08/01 | QBTS - 07/01 | QBTS - 06/02 | QBTS - 19/02 | QBTS - 08/01 | QBTS 19.02 | QBTS - 08/01 | QBTS - 21/03 | QBTS - 21/03
11 | Placement of Break Glass Units in accordance with AS1428.1 (Cl. 13) |  | QBTS 28.02 - QBUIL-GCOR-017771 | QBTS 24/06 | No Break Glass adjacent to FIP- Fire Engineer Confirmed not Required | No Break Glass adjacent to FIP- Fire Engineer Confirmed not Required | No Break Glass adjacent to FIP- Fire Engineer Confirmed not Required | QBTS - 07/01 | QBTS - 06/02 | QBTS - 19/02 | N/A | N/A | N/A | QBTS - 21/03 | QBTS - 21/03
12 | Glazing decals/ Visual indicators in accordance with AS1428.1 (CL6.6) | N/A | QBTS 28.02 - QBUIL-GCOR-017771 | QBTS 24/06 | N/A | N/A | N/A | QBTS Apporved 26/02 - JHG Confirmed 10/02 - (Glazing Strips Installed) I Issued to QBTS on Aconex | QBTS - 06/02 | QBTS - 19/02 | N/A | N/A | N/A | QBTS - 21/03 | QBTS - 21/03
13 | Door Forces to not exceed 20N in accordance with AS1428.1 - ISSUE EXMEPTION | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
14 | Latch side clearance (530mm MIN) in accordance with AS1428.1 | N/A | QBTS -05/02 | QBTS 24/06 | Checking whether dispensation applies | QBTS - 08/01 | QBTS - 08/01 | QBTS - 07/01 | QBTS - 06/02 | QBTS - 19/02 | QBTS - 08/01 | QBTS 19.02 | QBTS 03/12 | QBTS - 21/03 | QBTS - 21/03
15 | Installation of Emergency Egress Path Signage |  | SI Issued - Pending Fredon Adjustments JH-SI-002449 | QBTS 24/06 | SI Issued - Pending Fredon Adjustments JH-SI-002449 | QBTS - 08/01 | QBTS - 08/01 | QBTS Accepted WSP Advice 10/03 QBuil-GCOR-017887 | L.10 Exit Light Adjustments Required JH-GCOR-078804 | QBTS - 21/03 | QBTS - 08/01 | ` | QBTS - 27.02.24 QBUIL-GCOR-017747 | QBTS - 21/03 | QBTS - 21/03 - Items Actioned and Closeout
16 | Installation of Block Plan Signage | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03 | WSP Issuing Final Revision 24-25/03
17 | Installation of Fire Extinguishers & associated Extinguisher Signage |  | Missing Fire Blanket Signage - Actioned 20/03 JH-GCOR-078718 | QBTS 24/06 | 28.02 QBTS QBUIL-GCOR-01770 | QBTS - 08/01 | QBTS - 08/01 | QBTS - 07/01 | QBTS - 06/02 - Form 12s to Be Issued | QBTS - 19/02 | QBTS - 08/01 | QBTS 19.02 | QBTS 03/12 | Missing Fire Extinguishers
18 | Installation of HAZARD TAPE on equipment <2.1m within plantroom spaces | N/A | 14/02- QBUIL-GCOR-017585 | QBTS 24/06 | QBTS 28/01 - Linemarking Issued JH-GCOR-077675 | JHG- Ready for QBTS 28/01 | JHG- Ready for QBTS 28/01 | N/A - No Low Head-height equipment | Issued to QBTS 27.02 - Low Head Height Signage Required with Additional Hazard Tape | QBTS - 21/03 | N/A | QBTS 19.02 | N/A | N/A | JHG- Ready for QBTS 28/01
19 | Emergency Lighting Test register present at Switchboard & adequate LUX levels in accordance with AS2293. | Inspected Awaiting Defects Closeout | Inspected Awaiting Defects Closeout | Completed Defect Free | Inspected Awaiting Defects Closeout | Inspected Awaiting Defects Closeout | Inspected Awaiting Defects Closeout | Inspected Awaiting Defects Closeout | Inspected Awaiting Defects Closeout | Inspected Awaiting Defects Closeout | Completed Defect Free | Completed Defect Free | Completed Defect Free |  | Inspected Awaiting Defects Closeout
20 | Emergency Eye Wash / Shower Maintenance register | Check Onsite | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Commissioning Documents and Statement of Compliance - to be issued to QBTS | N/A | N/A | N/A | N/A | N/A
21 | General Stairs: Rise & Going Compliance |  | QBTS -05/02 | N/A | N/A | QBTS - 08/01 | QBTS - 08/01 | N/A | QBTS -Pending Contrast Strip to Office Post | Documentation to be Issued to QBTS | QBTS - 08/01 | QBTS 19.02 | N/A | N/A | N/A
22 | Plantroom Stairs: Rise & Going Compliance |  | QBTS -05/02 | N/A | QBTS - 10/01 | QBTS - 08/01 | QBTS - 08/01 | N/A | QBTS - 06/02 - Softcopy to be issued on Aconex | N/A | N/A | N/A | N/A | N/A | N/A
23 | Ramp Fall Compliance |  | N/A | N/A | N/A | N/A | N/A | N/A | Missing Handrails - Plant Area Rear Stairs (external) | Ready for QBTS - JHG Confirmed 28/01 (Officer Posts) | N/A | N/A | N/A | N/A | N/A
24 | Threshold Compliance |  | QBTS -05/02 | QBTS 24/06 | Entry- AG to Check |  | QBTS - 08/01 | Rectified Onsite - Pending Issue of Form 12 to Aconex. | Staff Dinning, D-L.01-B (Laundry), D-K.02-B (Bin Lock) D-K.01-A (Kitchen) and FM Store | JH-GCOR-078085 Workshop 3&4 Entrance Door Threshold Not Installed | QBTS - 08/01 | QBTS 19.02 | QBTS 20/01 | QBTS Accepted - 24/03 QBUIL-GCOR-018109 | QBTS - 21/03
25 | Tactiles | N/A [GBA-GCOR-005858] | QBTS -05/02 | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | N/A [GBA-GCOR-005858] | External Directional Tactiles - Directional on new concete behind SER and Reinstate Removed Section | N/A [GBA-GCOR-005858]
26 | Catwalks / suspended platform compliance | N/A | N/A | N/A | 28.02 QBTS QBUIL-GCOR-01770 | 28/01 JHG Confirmed Ready for QBTS | 28/01 JHG Confirmed Ready for QBTS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
27 | Roof Safety System Compliance |  | QBTS -05/02 - Issue Form 12s | Ready for QBTS - JHG Confirmed | Certification Confirmed on Aconex | QBTS - 08/01 - Softcopy to be issued on Aconex | QBTS - 08/01 - Softcopy to be issued on Aconex | Certification Confirmed on Aconex | QBTS - 06/02 - Softcopy to be issued on Aconex | Photo Compliance Plates and Issuing of Documents on Aconex | Photo Compliance Plates and Issuing of Documents on Aconex | Photo Compliance Plates and Issuing of Documents on Aconex | Documentation Issued on Aconex JH-TRANSMIT-007881
Witness Testing Points
1 | Fire Detection Witness Test | Witnessed - Rectification to be Commenced on Defect Items |  | Witnessed - Rectification to be Commenced on Defect Items | Scheduled for 20/01/25 | Scheduled for 23/01/25 | Scheduled for 23/01/25 | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Still Under Construction | Witnessed - Rectification to be Commenced on Defect Items
2 | EWIS SPL Testing & Strobe activation | Witnessed - Rectification to be Commenced on Defect Items |  | Witnessed - Rectification to be Commenced on Defect Items | Scheduled for 20/01/25 | Scheduled for 23/01/25 | Scheduled for 23/01/25 | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Still Under Construction | Witnessed - Rectification to be Commenced on Defect Items
3 | IST (Integrated Systems Test) Testing of Life Safety Services – E.g. HVAC Fire Matrix & Fire or Gas & Fire | Witnessed - Rectification to be Commenced on Defect Items |  | Witnessed - Rectification to be Commenced on Defect Items | Scheduled for 20/01/25 | Scheduled for 23/01/25 | Scheduled for 23/01/25 | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Still Under Construction | Witnessed - Rectification to be Commenced on Defect Items
4 | Wet Fire Systems: Purge & Deluge Testing | Witnessed - Rectification to be Commenced on Defect Items |  | Witnessed - Rectification to be Commenced on Defect Items | Scheduled for 20/01/25 | Scheduled for 23/01/25 | Scheduled for 23/01/25 | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Witnessed - Rectification to be Commenced on Defect Items | Still Under Construction | Witnessed - Rectification to be Commenced on Defect Items
5 | Response Times inline with FER | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage | To be completed in final stage

## Inspection Record
Building | Last Inspection Date | Attending Certifier | Report Issued | JHG Response | JHG Subbie Markup | Comments | Reinspection Date
C- Detention Unit | 2025-01-08 | SR | 2025-02-10 | 2025-02-20 | Issued
Q- Multifaith | 2025-01-07 | SR | 2025-02-10 | 2025-02-20 | Issued
S12- Secure Accomodation | 27/08 & 03/12 | SM | 2025-02-17 | 2025-02-20 | Issued
S34- Secure Accomodation | 27/08 & 03/12 | SM | 2025-02-14 | 2025-02-20 | Issued
S56- Secure Accomodation | 17/08 & 10/09 | SM | 2025-03-03 |  | Issued
ES - Entry Secure | 2025-01-08 | SR | 07/02 & 14/02 | 2025-02-11 | Issued
TH1 | 2025-02-06 | SR | 2025-02-14 |  | Issued
TH2 | 2025-02-11 | SR | 2025-02-14 |  | Issued
W- Industires | 2024-02-19 | SR SM | 2025-02-26 |  | Issued
KL - Kitchen Laundry | 2025-02-06 | SR | 2025-02-13 |  | Issued
A - Administration | 2024-06-24 | SM
GH- Gatehouse | 2024-02-05 | SM | 2024-02-07 |  | Issued
VI - Visits
MU- Medical Unit | 2025-01-08 | SR | 2025-02-18 | 2025-02-18 | Issued
PP - Prisioner Processing |  | SR | 2025-08-18 | 2025-02-18 | Issued
Y - Mental Health | 2025-01-10 | SR | 2025-02-14 |  | Issued
H1 - Sports Hall (Secure)
H2 - Sports Hall (Residential) | 2024-02-19 | SR SM
ER - Entry Residential | 2024-12-10 | SR | 2025-02-18
R1 - Residential Accomodation | 2025-01-20 | SR | 2025-02-18 |  | Issued
R2 - Residential Accomodation | 2025-01-20 | SR | 2025-02-18 |  | Issued
R3 - Residential Accomodation | 2025-01-20 | SR | 2025-02-18 |  | Issued
R4 - Residential Accomodation | 2025-01-20 | SR | 2025-02-18 |  | Issued
R5 - Residential Accomodation | 2024-02-19 | SR SM | 2025-02-25 |  | Issued
R6 - Residential Accomodation | 2025-01-20 | SR | 2025-02-18 |  | Issued
R7 - Residential Accomodation | 2024-12-10 | SR | 2025-02-18 |  | Issued
R8 - Residential Accomodation | 2024-12-10 | SR | 2025-02-18 |  | Issued
R9 - Residential Accomodation | 2024-12-10 | SR | 2025-02-18 |  | Issued
R10 - Residential Accomodation | 2024-12-10 | SR | 2025-02-18 |  | Issued
R11 - Residential Accomodation | 2024-12-10 | SR | 2025-02-18 |  | Issued
R12 - Residential Accomodation | 2024-12-10 | SR | 2025-02-18 |  | Issued
R13 - Residential Accomodation | 2024-12-10 | SR | 2025-02-18 |  | Issued
X23- External Administration | 2024-12-03 | SR
X1- Visitor Processing
X21 - Chiller Plant
X3 Pumphouse
X7 WWTP | COMPLETE
X3 Existing Gen Plant | COMPLETE
X9 Reference Cells | COMPLETE